## Request a quote
Request a quotation for TC-ER-HL
Application engineer · hazardous-location & offshore cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/tc-er-hl-instrumentation-tray-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
TC-ER-HL Instrumentation Tray Cable – Dimensions & weights (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tc-er-hl-instrumentation-tray-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1277 / UL 2225 / NEC Articles 336, 501.10(A) & 505. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Shielding | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| TC-ER-HL 1P×18AWG OS | 1 Pair × 18 AWG + GND | OS | 8.6 | 28 | 102 | 52 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 1T×18AWG OS | 1 Triad × 18 AWG + GND | OS | 9.2 | 36 | 118 | 55 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 2P×18AWG IS/OS | 2 Pairs × 18 AWG + GND | IS+OS | 11.8 | 52 | 178 | 71 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 4P×18AWG IS/OS | 4 Pairs × 18 AWG + GND | IS+OS | 14.2 | 96 | 265 | 85 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 8P×18AWG IS/OS | 8 Pairs × 18 AWG + GND | IS+OS | 18.6 | 182 | 445 | 112 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 12P×18AWG IS/OS | 12 Pairs × 18 AWG + GND | IS+OS | 22.1 | 268 | 615 | 133 | 18 AWG (0.82 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 1P×16AWG OS | 1 Pair × 16 AWG + GND | OS | 9.4 | 42 | 124 | 56 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 1T×16AWG OS | 1 Triad × 16 AWG + GND | OS | 10.1 | 56 | 145 | 61 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 2P×16AWG IS/OS | 2 Pairs × 16 AWG + GND | IS+OS | 12.8 | 78 | 212 | 77 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 4P×16AWG IS/OS | 4 Pairs × 16 AWG + GND | IS+OS | 15.6 | 146 | 326 | 94 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 8P×16AWG IS/OS | 8 Pairs × 16 AWG + GND | IS+OS | 20.4 | 278 | 548 | 122 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 12P×16AWG IS/OS | 12 Pairs × 16 AWG + GND | IS+OS | 24.4 | 410 | 765 | 146 | 16 AWG (1.31 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 1P×14AWG OS | 1 Pair × 14 AWG + GND | OS | 10.5 | 64 | 158 | 63 | 14 AWG (2.08 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 2P×14AWG IS/OS | 2 Pairs × 14 AWG + GND | IS+OS | 14.4 | 118 | 274 | 86 | 14 AWG (2.08 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 4P×14AWG IS/OS | 4 Pairs × 14 AWG + GND | IS+OS | 17.6 | 224 | 428 | 106 | 14 AWG (2.08 mm²) XHHW-2 — 600 V Type TC-ER-HL
| TC-ER-HL 8P×14AWG IS/OS | 8 Pairs × 14 AWG + GND | IS+OS | 23 | 428 | 725 | 138 | 14 AWG (2.08 mm²) XHHW-2 — 600 V Type TC-ER-HL
Every TC-ER-HL cable includes a dedicated green/yellow equipment grounding conductor per NEC 501.10(A)(1)(e).

## Electrical parameters by AWG ga
TC-ER-HL Instrumentation Tray Cable – Electrical parameters by AWG gauge (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tc-er-hl-instrumentation-tray-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1277 / UL 2225 / NEC Articles 336, 501.10(A) & 505. Values for your order are confirmed in the quotation.
AWG size (metric) | Equip. ground wire AWG | Max. DC R @ 20 °C Ω/km | Nom. C (core/core) pF/m | AC test V rms
18 AWG (0.82 mm² · 7×26) | 18 AWG | 21.9 | 82 | 2000
16 AWG (1.31 mm² · 7×24) | 16 AWG | 14 | 88 | 2000
14 AWG (2.08 mm² · 7×22) | 14 AWG | 8.9 | 94 | 2000
For multi-pair cables with overall diameter > 25.4 mm (1.0 in.) in Class I Division 1, specify MC-HL Instrumentation.

## Technical data
TC-ER-HL Instrumentation Tray Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/tc-er-hl-instrumentation-tray-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1277 / UL 2225 / NEC Articles 336, 501.10(A) & 505. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 600 V rms (UL 1277 TC-ER & UL 2225 -HL)
Key data | Hazardous area | Class I Div 1 (Zone 1 & Div 2 (NEC 501/505))
Key data | Crush & impact | 2000 lbf / 50 ft (UL 2225 HL severe impact test)
Key data | Temperature | −40…+90 °C (wet & dry · −40 °C cold impact)
Key data | Gas blocking | UL 2225 Gas Seal (blocked interstices + grounding)
Key data | Bend radius | 6 × OD (tighter & lighter than MC-HL)
Electrical | Rated voltage | 600 V rms (UL 1277 Type TC-ER-HL)
Electrical | Dielectric test voltage | 2000 V AC rms for 5 min (XHHW-2 conductors)
Electrical | Insulation resistance | ≥ 2000 MΩ·km at +20 °C
Electrical | Nominal mutual capacitance | ≈ 80–95 pF/m (XHHW-2 XLPE dielectric)
Thermal | Operating temperature | −40 °C to +90 °C (wet or dry)
Thermal | Cold bend & cold impact | Passes −40 °C cold bend and −25 °C / −40 °C impact
Mechanical | UL 2225 -HL crush test | ≥ 2,000 lbf (8,900 N) crush load without shorting
Mechanical | UL 2225 -HL impact test | ≥ 50 ft-lbf (68 J) falling weight impact
Mechanical | Max. cable OD for Class I Div 1 | ≤ 1.0 in. (25.4 mm) per NEC 501.10(A)(1)(e)
Mechanical | Min. bending radius | 6 × OD
Resistance | Flame test ratings | UL 1685 / IEEE 1202 (70,000 BTU/hr) · IEC 60332-3-22 Cat A · FT4
Resistance | Oil, mud & sunlight | UL Oil Res I & II · NEK 606 mud-resistant CPE option · Sun Res
Standards | Certification standards | UL 1277 & UL 2225 Listed Type TC-ER-HL
Standards | NEC & Coast Guard | NEC Art. 336, 501.10(A)(1)(e), 505.15(B) · USCG 46 CFR 111.60
Identification | Core identification | Black / White numbered pairs + Green/Yellow equipment ground
Identification | Outer jacket colour | Black (or Blue stripe for Ex-i)
Identification | Customs tariff (HS) | 8544.49

## Construction
TC-ER-HL Instrumentation Tray Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/tc-er-hl-instrumentation-tray-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1277 / UL 2225 / NEC Articles 336, 501.10(A) & 505. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded tinned copper conductors + ground | 18 AWG, 16 AWG or 14 AWG Class B/C stranded tinned copper pairs/triads plus full-sized insulated green/yellow equipment grounding conductor
2 | 600 V 90 °C XHHW-2 cross-linked polyethylene | Heavy-wall thermoset XLPE (UL 44 XHHW-2 rated +90 °C wet and dry)
3 | Individual & overall 100 % Al/PET shields | Isolated Aluminium/PET pair shields (IS) + overall Al/PET shield (OS) with tinned copper drain wires | 100 % electrostatic noise immunity
4 | UL 2225 gas/vapour-blocking core fillers | Non-wicking elastomeric interstitial blocking compound and circular polymeric inner bedding
5 | Heavy-duty UL 2225 -HL CPE / TPE outer jacket | Extra-heavy-duty cross-linked Chlorinated Polyethylene (CPE) or Arctic TPE, Black
| TC-ER-HL OS (Single Pair / Triad) | 600 V 1P or 1T + Equipment Ground with overall Al/PET shield and UL 2225 -HL jacket
| TC-ER-HL IS/OS (Multi-Pair) | 600 V 2P to 12P + Equipment Ground with individual & overall shields (OD ≤ 25.4 mm for Div 1)

## Quality and supply
TC-ER-HL Instrumentation Tray Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/tc-er-hl-instrumentation-tray-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1277 / UL 2225 / NEC Articles 336, 501.10(A) & 505. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 2000 V AC dielectric test & spark test — 2.0 kV AC for 5 min on XHHW-2 insulated conductors | Every manufactured reel
Sample test | UL 2225 Hazardous Location crush (2,000 lbf) & impact (50 ft-lbf) test — Pass MC-HL-equivalent mechanical crush and impact without metal armour | UL follow-up audit
Sample test | UL 2225 core gas/vapour tightness & IEEE 1202 flame test — Pass internal gas transmission limit and 70,000 BTU/hr vertical flame test | Periodic audit
Standard / approval | UL 1277 & UL 2225 Listed Type TC-ER-HL (600 V)
Standard / approval | NEC 501.10(A)(1)(e) Class I Div 1 & 505 Zone 1
Standard / approval | USCG 46 CFR 111.60 & ABS / DNV Offshore
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX <size> E-FILE (UL) TYPE TC-ER-HL XHHW-2 600V 90C WET/DRY SUN RES OIL RES I/II DIR BUR FT4
Supply | Delivery form: Non-returnable fumigated wooden drums
Supply | Standard lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP