## Request a quote
Request a quotation for TC / TC-ER
Application engineer · North American UL/NEC tray cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/tc-tc-er-industrial-tray-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
TC / TC-ER TC/TC-ER Industrial Tray Cable – Dimensions & weights (23)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tc-tc-er-industrial-tray-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1277 / NEC Art. 336 (TC-ER). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| TC-ER 3C 18 AWG (0.75 mm²) | 3×0.75 | 18 | 6.5 | 7.1 | 21 | 72 | 36 | 18 AWG (≈ 0.75 mm²) 600 V Control Tray Configurations
| TC-ER 5C 18 AWG (0.75 mm²) | 5×0.75 | 18 | 7.5 | 8.2 | 36 | 102 | 41 | 18 AWG (≈ 0.75 mm²) 600 V Control Tray Configurations
| TC-ER 9C 18 AWG (0.75 mm²) | 9×0.75 | 18 | 9.6 | 10.4 | 64 | 162 | 52 | 18 AWG (≈ 0.75 mm²) 600 V Control Tray Configurations
| TC-ER 12C 18 AWG (0.75 mm²) | 12×0.75 | 18 | 10.8 | 11.7 | 86 | 206 | 58 | 18 AWG (≈ 0.75 mm²) 600 V Control Tray Configurations
| TC-ER 19C 18 AWG (0.75 mm²) | 19×0.75 | 18 | 12.7 | 13.8 | 136 | 304 | 69 | 18 AWG (≈ 0.75 mm²) 600 V Control Tray Configurations
| TC-ER 3C 16 AWG (1.5 mm²) | 3×1.5 | 16 | 7.3 | 7.9 | 43 | 95 | 40 | 16 AWG (≈ 1.5 mm²) 600 V Control Tray Configurations
| TC-ER 5C 16 AWG (1.5 mm²) | 5×1.5 | 16 | 8.5 | 9.2 | 72 | 138 | 46 | 16 AWG (≈ 1.5 mm²) 600 V Control Tray Configurations
| TC-ER 9C 16 AWG (1.5 mm²) | 9×1.5 | 16 | 10.8 | 11.7 | 129 | 224 | 58 | 16 AWG (≈ 1.5 mm²) 600 V Control Tray Configurations
| TC-ER 12C 16 AWG (1.5 mm²) | 12×1.5 | 16 | 12.8 | 13.9 | 172 | 298 | 70 | 16 AWG (≈ 1.5 mm²) 600 V Control Tray Configurations
| TC-ER 19C 16 AWG (1.5 mm²) | 19×1.5 | 16 | 15 | 16.3 | 273 | 442 | 82 | 16 AWG (≈ 1.5 mm²) 600 V Control Tray Configurations
| TC-ER 3C 14 AWG (2.5 mm²) | 3×2.5 | 14 | 8 | 8.7 | 72 | 122 | 44 | 14 AWG (≈ 2.5 mm²) 600 V Control & Branch Tray Configurations
| TC-ER 4C 14 AWG (2.5 mm²) | 4×2.5 | 14 | 8.7 | 9.5 | 96 | 152 | 48 | 14 AWG (≈ 2.5 mm²) 600 V Control & Branch Tray Configurations
| TC-ER 7C 14 AWG (2.5 mm²) | 7×2.5 | 14 | 10.5 | 11.4 | 168 | 236 | 57 | 14 AWG (≈ 2.5 mm²) 600 V Control & Branch Tray Configurations
| TC-ER 12C 14 AWG (2.5 mm²) | 12×2.5 | 14 | 14 | 15.2 | 288 | 398 | 76 | 14 AWG (≈ 2.5 mm²) 600 V Control & Branch Tray Configurations
| TC-ER 19C 14 AWG (2.5 mm²) | 19×2.5 | 14 | 16.4 | 17.8 | 456 | 595 | 89 | 14 AWG (≈ 2.5 mm²) 600 V Control & Branch Tray Configurations
| TC-ER 4C 12 AWG (4 mm²) | 4×4 | 12 | 9.8 | 10.6 | 153 | 208 | 53 | 12 AWG (≈ 4.0 mm²) 600 V Power & Control Tray Configurations
| TC-ER 7C 12 AWG (4 mm²) | 7×4 | 12 | 11.8 | 12.8 | 268 | 332 | 64 | 12 AWG (≈ 4.0 mm²) 600 V Power & Control Tray Configurations
| TC-ER 12C 12 AWG (4 mm²) | 12×4 | 12 | 15.7 | 17.1 | 460 | 558 | 86 | 12 AWG (≈ 4.0 mm²) 600 V Power & Control Tray Configurations
| TC-ER 4C 10 AWG (6 mm²) | 4×6 | 10 | 11.6 | 12.6 | 230 | 298 | 63 | 10 AWG to 2 AWG (6–35 mm²) 600 V Feeder Tray Configurations
| TC-ER 4C 8 AWG (10 mm²) | 4×10 | 8 | 14.9 | 16.2 | 384 | 495 | 81 | 10 AWG to 2 AWG (6–35 mm²) 600 V Feeder Tray Configurations
| TC-ER 4C 6 AWG (16 mm²) | 4×16 | 6 | 17.3 | 18.8 | 614 | 735 | 94 | 10 AWG to 2 AWG (6–35 mm²) 600 V Feeder Tray Configurations
| TC-ER 4C 4 AWG (25 mm²) | 4×25 | 4 | 20.6 | 22.4 | 960 | 1110 | 112 | 10 AWG to 2 AWG (6–35 mm²) 600 V Feeder Tray Configurations
| TC-ER 4C 2 AWG (35 mm²) | 4×35 | 2 | 23.6 | 25.6 | 1344 | 1520 | 128 | 10 AWG to 2 AWG (6–35 mm²) 600 V Feeder Tray Configurations
Dimensions and weights are typical values per UL 1277 / NEC Art. 336 (TC-ER). Minimum fixed bending radius shown is 5 × OD.

## Electrical & current ratings
TC / TC-ER TC/TC-ER Industrial Tray Cable – Electrical & current ratings (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tc-tc-er-industrial-tray-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1277 / NEC Art. 336 (TC-ER). Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single pair/core 30 °C, A | Multi-core bundle 30 °C, A
0.75 | 18 | 26 | 12.0 | 10.0
1.5 | 16 | 13.3 | 23.0 | 18.0
2.5 | 14 | 7.98 | 30.0 | 25.0
4 | 12 | 4.95 | 41.0 | 34.0
6 | 10 | 3.3 | 53.0 | 44.0
10 | 8 | 1.91 | 74.0 | 61.0
16 | 6 | 1.21 | 99.0 | 82.0
25 | 4 | 0.78 | 131.0 | 108.0
35 | 2 | 0.554 | 162.0 | 135.0
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / DIN VDE 0891-1. Apply grouping derating factors for multi-core control and signal bundles.

## Technical data
TC / TC-ER TC/TC-ER Industrial Tray Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/tc-tc-er-industrial-tray-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1277 / NEC Art. 336 (TC-ER). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 600 V (UL 1277 · NEC Art. 336 Type TC-ER)
Key data | Thermal rating | 90 °C / 75 °C (90 °C dry · 75 °C wet (THHN/THWN-2))
Key data | Exposed Run | TC-ER rated (UL 1277 crush & impact rated)
Key data | Flame test | UL 1685 / FT4 (70,000 BTU/hr vertical tray flame test)
Key data | Bending radius | 5–8 × OD (5 × OD unshielded · 8 × OD shielded)
Key data | Size range | 18–2 AWG (0.75–35 mm² · 2 to 37 conductors)
Electrical | Rated voltage | 600 V RMS
Electrical | Dielectric test voltage | 2000 V – 3500 V AC per UL 83 / UL 1277
Electrical | Insulation resistance | ≥ 500 MΩ·km at +20 °C
Thermal | Max. conductor temperature | +90 °C dry · +75 °C wet (THHN/THWN-2) / +90 °C wet & dry (XHHW-2)
Thermal | Cold bend / impact rating | −25 °C cold impact · −40 °C fixed service
Thermal | Short-circuit temperature | +150 °C (THHN/THWN-2) · +250 °C (XHHW-2 XLPE)
Mechanical | Exposed Run (TC-ER) | Passes UL 1277 crush (2000 lbf) and impact tests for open tray-to-machine drops
Mechanical | Min. bending radius | 5 × OD (unshielded ≤ 25 mm) · 8 × OD (shielded)
Mechanical | Pulling tension | Max. 0.008 lbf/cmil (≈ 70 N/mm² on copper area) in tray pulls
Resistance | Vertical tray flame test | UL 1685 (70,000 BTU/hr) · IEEE 1202 / CSA FT4
Resistance | Oil resistance | UL Oil Res I (+60 °C) & Oil Res II (+75 °C) optional
Resistance | Outdoor & direct burial | 720-hour xenon-arc Sunlight Resistant & Direct Burial rated
Standards | Primary standard | UL 1277 (Type TC / TC-ER)
Standards | Installation code | NFPA 70 National Electrical Code (NEC) Article 336, Class I Div 2 per NEC 501.10(B)
Standards | Core identification | ICEA S-73-532 / NEMA WC 57 Method 1 (Table E1/E2 colour code) or Method 4 (numbered black)
Standards | RoHS & REACH | RoHS 2 & REACH compliant
Identification | Jacket colour | Black (UV-stabilised)
Identification | Conductor identification | ICEA Method 1 (Black, Red, Blue, Orange, Yellow, Brown…) or Method 4 numbered + Green GND
Identification | Jacket print legend | TEBAOFLEX (UL) E-FILE TYPE TC-ER 600V THHN/THWN-2 90C DRY 75C WET SUN RES DIR BUR FT4
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
TC / TC-ER TC/TC-ER Industrial Tray Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/tc-tc-er-industrial-tray-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1277 / NEC Art. 336 (TC-ER). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded bare copper conductor | ASTM B3 / B8 Class B (7-strand) or flexible Class K annealed bare copper from 18 AWG to 2 AWG | ASTM B3 / B8 · UL 1277
2 | THHN/THWN-2 or XHHW-2 insulation | Heat- and moisture-resistant PVC with polyamide nylon skin (UL 83 THHN/THWN-2) or cross-linked polyethylene (UL 44 XHHW-2) | UL 83 / UL 44 · 90 °C Dry / 75 °C Wet
3 | Cabled core bundle + ripcord | Conductors cabled with non-hygroscopic fillers, binder tape and high-strength nylon jacket ripcord | UL 1277
4 | Optional foil / braid shield | Unshielded standard, or 100 % Al/Mylar tape + tinned-copper drain wire / braid for shielded TC-ER control | UL 1277
5 | Sunlight- & oil-resistant PVC jacket | Heavy-duty black polyvinyl chloride jacket meeting UL Oil Res I/II, sunlight resistance and Direct Burial | UL 1277 · UL 1685 / FT4
| TC-ER THHN/THWN-2 Unshielded (18–2 AWG) | 600 V PVC/nylon insulated industrial power and control tray cable with ICEA colour/number code
| TC-ER Shielded (OAS / Foil + Braid) | 600 V overall-shielded instrumentation and PLC control tray cable for EMI-heavy plant trays
| TC-ER XHHW-2 XLPE (90 °C Wet/Dry) | Cross-linked polyethylene (XLPE) insulated tray cable rated +90 °C in both wet and dry locations

## Quality and supply
TC / TC-ER TC/TC-ER Industrial Tray Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/tc-tc-er-industrial-tray-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1277 / NEC Art. 336 (TC-ER). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 2.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / UL 1277 / NEC Art. 336 (TC-ER) (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath material physical properties — UL 1277 / NEC Art. 336 (TC-ER) | Type approval
Standard / approval | UL 1277 / NEC Art. 336 (TC-ER)
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (UL) TYPE TC-ER 600V THHN/THWN-2 90C DRY 75C WET SUN RES DIR BUR FT4
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pair counts or sheath colours on request