## Request a quote
Request a quotation for TECK90
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/teck90-armoured-industrial-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
TECK90 Armoured Industrial Cable – Dimensions & masses (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/teck90-armoured-industrial-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CSA C22.2 No. 131 / CEC Part I. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cores × AWG/MCM (1kV) | Bond Wire / CEC 90°C A | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| TECK90 3C 14 AWG | 3C × 14 AWG | 14 AWG Bond · 25 A | 15.8 | 68 | 295 | 110.6 | TECK90 size schedule
| TECK90 3C 12 AWG | 3C × 12 AWG | 14 AWG Bond · 30 A | 16.9 | 98 | 345 | 118.3 | TECK90 size schedule
| TECK90 3C 10 AWG | 3C × 10 AWG | 12 AWG Bond · 40 A | 18.4 | 152 | 430 | 128.8 | TECK90 size schedule
| TECK90 3C 8 AWG | 3C × 8 AWG | 10 AWG Bond · 55 A | 21.2 | 240 | 585 | 148.4 | TECK90 size schedule
| TECK90 3C 6 AWG | 3C × 6 AWG | 8 AWG Bond · 75 A | 24.1 | 382 | 810 | 168.7 | TECK90 size schedule
| TECK90 3C 4 AWG | 3C × 4 AWG | 8 AWG Bond · 95 A | 27.2 | 565 | 1080 | 190.4 | TECK90 size schedule
| TECK90 3C 2 AWG | 3C × 2 AWG | 6 AWG Bond · 130 A | 30.8 | 895 | 1520 | 215.6 | TECK90 size schedule
| TECK90 3C 1/0 AWG | 3C × 1/0 AWG | 6 AWG Bond · 170 A | 35.8 | 1360 | 2180 | 250.6 | TECK90 size schedule
| TECK90 3C 2/0 AWG | 3C × 2/0 AWG | 6 AWG Bond · 195 A | 38.4 | 1685 | 2610 | 268.8 | TECK90 size schedule
| TECK90 3C 3/0 AWG | 3C × 3/0 AWG | 4 AWG Bond · 225 A | 41.2 | 2160 | 3210 | 288.4 | TECK90 size schedule
| TECK90 3C 4/0 AWG | 3C × 4/0 AWG | 4 AWG Bond · 260 A | 44.5 | 2670 | 3880 | 311.5 | TECK90 size schedule
| TECK90 3C 250 MCM | 3C × 250 MCM | 4 AWG Bond · 290 A | 48.2 | 3110 | 4490 | 337.4 | TECK90 size schedule
| TECK90 3C 350 MCM | 3C × 350 MCM | 3 AWG Bond · 350 A | 53.6 | 4310 | 5980 | 375.2 | TECK90 size schedule
| TECK90 3C 500 MCM | 3C × 500 MCM | 2 AWG Bond · 430 A | 60.5 | 6110 | 8190 | 423.5 | TECK90 size schedule
Dimensions and tolerances conform to CSA C22.2 No. 131 / CEC Part I.

## Electrical data
TECK90 Armoured Industrial Cable – Electrical data (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/teck90-armoured-industrial-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CSA C22.2 No. 131 / CEC Part I. Values for your order are confirmed in the quotation.
Cores × AWG/MCM (1kV) | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
3C × 14 AWG | 8.45 | 25 | 20
3C × 12 AWG | 5.31 | 30 | 24
3C × 10 AWG | 3.34 | 40 | 32
3C × 8 AWG | 2.1 | 55 | 44
3C × 6 AWG | 1.32 | 75 | 60
3C × 4 AWG | 0.83 | 95 | 76
3C × 2 AWG | 0.52 | 130 | 104
3C × 1/0 AWG | 0.328 | 170 | 136
3C × 2/0 AWG | 0.261 | 195 | 156
3C × 3/0 AWG | 0.207 | 225 | 180
3C × 4/0 AWG | 0.164 | 260 | 208
3C × 250 MCM | 0.139 | 290 | 232
3C × 350 MCM | 0.099 | 350 | 280
3C × 500 MCM | 0.07 | 430 | 344
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
TECK90 Armoured Industrial Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/teck90-armoured-industrial-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CSA C22.2 No. 131 / CEC Part I. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage ratings | 600 V / 1000 V / (Control, LV & MV feeders)
Key data | Core insulation | RW90 XLPE (+90 ° (90 °C wet & dry thermoset)
Key data | Dual jackets | PVC inner + PVC (Full moisture seal under armour)
Key data | Armour | Interlocked Al ( (Or galvanized steel (SIA) option)
Key data | Temp window | -40 to +90 °C (CSA -40 °C cold impact & bend)
Key data | Min. bend radius | 7 × / 12 × cable (12× during pull · 7× final dress)
Electrical | Rated voltage | 600 V (control) · 1,000 V (LV power) · 5,000 V (MV power)
Electrical | Dielectric test voltage (1000 V grade) | 3.5 kV AC rms for 5 minutes
Electrical | Max. conductor temperature | +90 °C wet or dry · +130 °C emergency overload · +250 °C short-circuit
Thermal | Low-temperature installation & service | -40 °C cold bend and -40 °C cold impact per CSA C22.2 No. 0.3
Thermal | Continuous operating window | -40 °C to +90 °C
Mechanical | Minimum bending radius | 12 × OD during pulling · 7 × OD final trained bend
Mechanical | Crush & impact protection | Interlocked AIA armour + dual PVC jackets pass CSA heavy crush & impact
Resistance | Flame & acid-gas emission | CSA FT4 vertical tray flame (UL 1685) & AG14 (<14 % HCl acid gas)
Resistance | Hazardous location ('HL') rating | CSA HL approved for Class I Div 2, Class II Div 1 & 2, and Class III (and CEC Zone 1/2)
Standards | Governing standards | CSA C22.2 No. 131, CSA C22.2 No. 38 (RW90) & Canadian Electrical Code (CEC)
Standards | NEC / UL cross-compliance | UL 1569 Type MC / UL 1277 dual-listed options available
Identification | Phase core colour code | 3C: Red, Black, Blue · 4C: Red, Black, Blue, White (+ bare Cu bond)
Identification | Outer jacket voltage colour | Orange (600 V) · Black (1000 V) · Yellow (5000 V)

## Construction
TECK90 Armoured Industrial Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/teck90-armoured-industrial-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CSA C22.2 No. 131 / CEC Part I. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class B stranded copper + bare Cu bond | Compressed concentric stranded annealed copper phase conductors plus uninsulated stranded copper equipment bonding conductor | CSA C22.2 No. 131
2 | RW90 cross-linked polyethylene (XLPE) | Thermoset XLPE insulation rated +90 °C dry and wet (+250 °C short-circuit), colour-coded Black, Red, Blue (+ White) | CSA C22.2 No. 38
3 | Extruded PVC inner bedding jacket | -40 °C lead-free flame-retardant PVC inner jacket sealing the core assembly against moisture and corrosive gases | CSA C22.2 No. 131
4 | Interlocking aluminum armour (AIA) | Helically interlocked 5052 aluminum alloy (or galvanized steel) strip armour providing high crush and impact protection | CSA C22.2 No. 131
5 | FT4 / AG14 outer PVC jacket | Sunlight-, oil-, acid- and -40 °C cold-impact-resistant outer PVC sheath (Black for 1000 V, Orange for 600 V, Yellow for 5 kV) | CSA C22.2 No. 131
| 600 V Control & Multi-Conductor TECK90 (14 AWG to 10 AWG — 2C to 50C, Orange Jacket) | Multi-core control and instrumentation TECK90 with numbered or colour-coded XLPE cores.
| 1000 V 3-Core & 4-Core Power TECK90 (14 AWG to 750 MCM, Black Jacket) | Standard 3-conductor and 4-conductor + bare ground industrial feeder TECK90.
| 5 kV Unshielded / Shielded MV TECK90 (6 AWG to 500 MCM, Yellow Jacket) | Medium-voltage 5,000 V TECK90 feeder cable for mine distribution and large MV motors.

## Quality and supply
TECK90 Armoured Industrial Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/teck90-armoured-industrial-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CSA C22.2 No. 131 / CEC Part I. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC dielectric test, spark test & DC resistance — Zero breakdown; resistance per CSA C22.2 No. 131 | 100 % of reels
Sample test | -40 °C cold impact, -40 °C cold bend & XLPE hot-set — Passes -40 °C arctic hammer impact without jacket cracking | Every batch
Type test | CSA FT4 vertical tray flame, AG14 acid gas & HL crush test — CSA Certified Type TECK90 to C22.2 No. 131 | Type qualification
Standard / approval | CSA C22.2 No. 131 Type TECK90
Standard / approval | CSA FT4 Vertical Tray Flame
Standard / approval | CSA HL (Hazardous Location) Rated
Standard / approval | AG14 Low Acid Gas (<14 %)
Standard / approval | RoHS 3 Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX CSA TECK90 [N/C AWG] 1000V (-40C) XLPE HL FT4 AG14 SUN RES [lot/m]
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP