## Request a quote
Request a quotation for TPT & TPT-CW/SB / TP(OS)PNBS
Share pair/triad/quad count, conductor size (mm² or AWG), collective vs. individual+collective screen (c/i or OS/IS) and sheath grade.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/tpt-tpt-cw-sb-tp-os-pnbs/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
TPT, TPT-CW/SB & TP(OS)PNBS 300/600 V IEEE 1580 Type P Overall Shielde – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tpt-tpt-cw-sb-tp-os-pnbs/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| TPT 2×2×0.75 mm² | 2 × 2 × 0.75 mm² (2Pr) | Stranded Cu/SnCu (IEC 60228 Class 2/5) | 11.4 | 195 | 1.2 | 70 | TPT & TPT-CW/SB / TP(OS)PNBS Construction Schedule (−40…+125 °C)
| TPT 4×2×1.0 mm² | 4 × 2 × 1.0 mm² (4Pr) | Stranded Cu/SnCu (IEC 60228 Class 2/5) | 15.6 | 365 | 2.4 | 95 | TPT & TPT-CW/SB / TP(OS)PNBS Construction Schedule (−40…+125 °C)
| TPT 8×2×1.5 mm² | 8 × 2 × 1.5 mm² (8Pr) | Stranded Cu/SnCu (IEC 60228 Class 2/5) | 22.8 | 760 | 4.8 | 140 | TPT & TPT-CW/SB / TP(OS)PNBS Construction Schedule (−40…+125 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS).

## Electrical, optical & thermal p
TPT, TPT-CW/SB & TP(OS)PNBS 300/600 V IEEE 1580 Type P Overall Shielde – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tpt-tpt-cw-sb-tp-os-pnbs/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS). Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
2 × 2 × 0.75 mm² (2Pr) | 26 | 300/600 V (≤60 nF/km) | −40…+125 °C
4 × 2 × 1.0 mm² (4Pr) | 19.5 | 300/600 V (≤65 nF/km) | −40…+125 °C
8 × 2 × 1.5 mm² (8Pr) | 13.3 | 300/600 V (≤75 nF/km) | −40…+125 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
TPT, TPT-CW/SB & TP(OS)PNBS 300/600 V IEEE 1580 Type P Overall Shielde – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/tpt-tpt-cw-sb-tp-os-pnbs/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/600 V (Tested per IEEE 1580 Type P / UL 1309)
Key data | Operating temp. | −40…+125 °C (Continuous shipboard & offshore service)
Key data | Min. bend radius | 6 × OD (Marine tray, bulkhead & deck routing)
Key data | Core / conductor | Flexible Tinned (19-strand tinned copper with 125 °C XLPO)
Key data | Outer protection | Arctic Type P Mu (Heavy-duty thermoset outer sheath for of)
Key data | Standard | IEEE 1580 Type P (IEEE 1580 Type P & UL 1309 Overall Foil-)
Electrical | Rated voltage / transmission duty | 300/600 V (IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS))
Electrical | Core / conductor construction | Flexible Tinned Copper Pairs (4Pr × 16 AWG) — 19-strand tinned copper with 125 °C XLPO Black/White numbered insulation
Electrical | Primary dielectric / buffering | 100% Overall Al/PET Shield & Drain (OS) — Collective aluminum/polyester tape shield with tinned copper drain wire
Thermal | Continuous operating temperature | −40…+125 °C (shipboard & offshore duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS)
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Arctic Type P Mud-Resistant Jacket — Heavy-duty thermoset outer sheath for offshore drilling rigs
Mechanical | Minimum bending radius | 6 × OD
Mechanical | Armour, screen & mechanical duty | Bronze / Copper Wire Braid (SB / -CW) — Braided bronze or tinned copper mechanical armour
Resistance | Flame, fire & smoke performance | Qualified for marine flame-retardance and low-smoke zero-halogen / fire safety per IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS)
Resistance | Oil, drilling mud & seawater resistance | Resistant to marine fuel/lube oils, salt mist and offshore fluids per IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS)
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS)
Standards | Environmental & test standards | IEC 60228 / IEC 60332-3-22 / IEC 60754 / IEC 61034 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | TPT & TPT-CW/SB / TP(OS)PNBS
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Arctic Type P Mu)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
TPT, TPT-CW/SB & TP(OS)PNBS 300/600 V IEEE 1580 Type P Overall Shielde – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/tpt-tpt-cw-sb-tp-os-pnbs/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible Tinned Copper Pairs (4Pr × 16 A | 19-strand tinned copper with 125 °C XLPO Black/White numbered insulation
2 | 100% Overall Al/PET Shield & Drain (OS) | Collective aluminum/polyester tape shield with tinned copper drain wire
3 | Thermoset Inner Bedding Jacket | Flame-retardant elastomeric inner sheath isolating shield from armour
4 | Bronze / Copper Wire Braid (SB / -CW) | Braided bronze or tinned copper mechanical armour
5 | Arctic Type P Mud-Resistant Jacket | Heavy-duty thermoset outer sheath for offshore drilling rigs
| TPT & TPT-CW/SB / TP(OS)PNBS — Standard Shipboard & Offshore Execution | Built to IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS) with flexible tinned copper pairs (4pr × 16 awg) and arctic type p mud-resistant jacket
| TPT & TPT-CW/SB / TP(OS)PNBS — Custom Drum Length & Gland Kit | Available in custom continuous shipboard/offshore drum lengths or with marine EMC cable glands
| TPT & TPT-CW/SB / TP(OS)PNBS — Class & Routine Test Certified | Supplied with EN 10204 3.1 routine dielectric, conductor resistance & flame/fire test report

## Quality and supply
TPT, TPT-CW/SB & TP(OS)PNBS 300/600 V IEEE 1580 Type P Overall Shielde – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/tpt-tpt-cw-sb-tp-os-pnbs/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS)) — DC resistance at 20 °C / optical attenuation and outer diameter within IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS) tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS)) — Zero dielectric breakdown and verified insulation resistance for 300/600 V rating | Every manufactured drum length
Type test | Flame, fire integrity, oil/mud & mechanical qualification (IEEE 1580 Type P & UL 1309 Overall Foil-Shielded (OS)) — Verified flame/fire performance, fluid resistance and thermal stability across −40…+125 °C | Type qualification & periodic lot audit
Standard / approval | IEEE 1580 Type P / UL 1309 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX TPT & TPT-CW/SB / TP(OS)PNBS IEEE 1580 Type P / UL 1309 300/600 V CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel marine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shipboard/offshore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP