## Request a quote
Request a quotation for TT1000 / TT1100-OHP
Application engineer · instrumentation & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/tracetek-tt1000-tt1100-ohp-conductive-polymer-water-leak-detection-sensing-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
TT1000 / TT1100-OHP Conductive-Polymer Water Leak Sensing Cable – Dimensions & sensing performance (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt1000-tt1100-ohp-conductive-polymer-water-leak-detection-sensing-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on UL 719 / NFPA 75 / EN 50174-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Installation environment | Outer Ø mm | Weight ≈ kg/km | Sense R Ω/m | Wetted alarm mm | Series
| TT1000 (Bulk) | Raised Floor, Drip Pan & Plenum Subfloor | 6 | 34 | 20 | 50 | 4-Wire Conductive-Polymer Water Leak Sensing Cables
| TT1000-PC (Modular) | Pre-Terminated 3 m / 7.5 m / 15 m / 30 m Plug-and-Play | 6 | 34 | 20 | 50 | 4-Wire Conductive-Polymer Water Leak Sensing Cables
| TT1100-OHP (Bulk) | Overhead Pipe Under-Insulation / Belly Strap | 7.5 | 42 | 20 | 20 | 4-Wire Conductive-Polymer Water Leak Sensing Cables
| TT1100-OHP-PC | Pre-Terminated Overhead Pipe Modular Assemblies | 7.5 | 42 | 20 | 20 | 4-Wire Conductive-Polymer Water Leak Sensing Cables
Directly compatible with 4-wire locating controllers (TTDM-128, TTSIM-1/2, and standard 20 Ω/m Modbus/BACnet leak transmitters).

## Technical data
TT1000 / TT1100-OHP Conductive-Polymer Water Leak Sensing Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt1000-tt1100-ohp-conductive-polymer-water-leak-detection-sensing-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on UL 719 / NFPA 75 / EN 50174-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Architecture | 4-Wire Locating (2 sense + 2 signal/loop wires)
Key data | Sensor resistance | ≈ 20.0 Ω/m (Precision linear ohm/m gradient)
Key data | Location accuracy | ± 0.5 % of lengt (Typically ±0.5 m to ±1.0 m)
Key data | Outer diameter | 6.0 mm (TT1000) (7.5 mm (TT1100-OHP braided))
Key data | Plenum flame | NFPA 262 / UL 91 (Safe in air-handling plenums)
Key data | Reset time | Wipes dry in sec (Hydrophobic fluoropolymer core)
Electrical | Sensing wire linear R | ≈ 20.0 Ω/m (±2 % per metre for accurate distance readout)
Electrical | Continuity wire DC R | ≈ 0.14 Ω/m (26 AWG stranded tinned copper)
Electrical | Dry insulation resistance | ≥ 100 MΩ per 30 m sensing circuit
Electrical | Max. sensing circuit length | Up to 150 m per TTSIM / TTDM-128 sensor interface module
Thermal | Continuous operating temp. | -20 °C to +75 °C (TT1000) · 0 °C to +75 °C (TT1100-OHP)
Thermal | Storage temperature | -40 °C to +85 °C
Thermal | Plenum fire rating | UL 910 / NFPA 262 plenum flame & low smoke qualified (TT1000)
Mechanical | Outer diameter | 6.0 mm / 0.24 in (TT1000) · 7.5 mm / 0.30 in (TT1100-OHP)
Mechanical | Min. bend radius | 25 mm (4 × OD)
Mechanical | Crush resistance | > 180 kg on 12 mm flat plate without shorting
Resistance | Detected liquids | Potable water, chilled water, condensate, glycol/water mixes
Resistance | Dry-out & reset | TT1000 resets within seconds of wiping dry; zero water absorption
Resistance | Dust & metal floor immunity | Recessed flutes prevent contact with flat metal subfloors
Standards | Data-centre protection | NFPA 75 & EN 50600-2-2 / EN 50174-2
Standards | Plenum cable listing | NFPA 262 (UL 910) & UL 61010-1 system interface
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Core / braid colour | TT1000: Yellow core / Black sense wires · TT1100-OHP: White/Grey wicking braid
Identification | Customs tariff (HS) | 8544.4290
Identification | Modular connectivity | Supplied as bulk reel or pre-terminated modular lengths (1.5 m to 30 m)

## Construction
TT1000 / TT1100-OHP Conductive-Polymer Water Leak Sensing Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt1000-tt1100-ohp-conductive-polymer-water-leak-detection-sensing-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on UL 719 / NFPA 75 / EN 50174-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 2 × insulated copper reference & loop-continuity wires | 2 × 26 AWG stranded tinned copper conductors insulated with colour-coded fluoropolymer (Red & Green/White)
2 | Fluted non-conductive fluoropolymer central carrier core | High-visibility Yellow (TT1000) fluted fluoropolymer central profile locking the 4 helical wires at fixed spacing
| TT1000 (6.0 mm Underfloor) | Smooth high-visibility Yellow 4-wire conductive-polymer water sensing cable for raised floors & drip pans
| TT1100-OHP (7.5 mm Overhead Pipe) | Wicking-braided 4-wire water sensing cable for strapping under overhead chilled-water & domestic water pipes

## Quality and supply
TT1000 / TT1100-OHP Conductive-Polymer Water Leak Sensing Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt1000-tt1100-ohp-conductive-polymer-water-leak-detection-sensing-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on UL 719 / NFPA 75 / EN 50174-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % linear resistance gradient (Ω/m) & continuity test — 20.0 Ω/m ± 2 % across entire length for sub-metre location accuracy | Every manufactured reel / assembly
Routine test | Dry insulation resistance & tap-water response time test — Dry IR ≥ 100 MΩ and alarm response < 5 s upon 50 mm water bridge | Every production lot
Type test | NFPA 262 (UL 910) Steiner tunnel plenum flame & smoke test — Max flame spread ≤ 1.5 m, peak optical smoke density ≤ 0.50 | Qualification test
Standard / approval | NFPA 262 / UL 910 Plenum
Standard / approval | NFPA 75 Data-Centre Compliant
Standard / approval | CE, RoHS 2 & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | Tag & connector print: TEBAOFLEX TT1000 / TT1100-OHP
Supply | Delivery form: Fumigated wooden drums, steel reels or precision spools
Supply | Standard lengths: 500 m · 1000 m (or custom cut/spooled lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP