## Request a quote
Request a quotation for TX / Type T extension
Application engineer · cryogenic, LNG & pharma instrumentation
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/tx-thermocouple-extension-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
TX / Type T extension Thermocouple Cable – Dimensions, construction & weights (15)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Insulation / Sheath | Temp. range | Outer Ø ≈ mm | Weight ≈ kg/km | Min. bend R fixed mm | Series
| TX-PVC-OS 1×2×0.5 | 1×2×0.5 mm² (7/0.30) | PVC / PVC (OS) | −25…+100 °C | 5.6 | 44 | 42 | TX PVC / PVC Screened Process Cables (−25…+100 °C)
| TX-PVC-PiMF 2×2×0.5 | 2×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+100 °C | 8.6 | 84 | 64 | TX PVC / PVC Screened Process Cables (−25…+100 °C)
| TX-PVC-PiMF 4×2×0.5 | 4×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+100 °C | 10.8 | 142 | 81 | TX PVC / PVC Screened Process Cables (−25…+100 °C)
| TX-PVC-PiMF 8×2×0.5 | 8×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+100 °C | 14.1 | 246 | 106 | TX PVC / PVC Screened Process Cables (−25…+100 °C)
| TX-PVC-PiMF 12×2×0.5 | 12×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+100 °C | 16.9 | 348 | 127 | TX PVC / PVC Screened Process Cables (−25…+100 °C)
| TX-PVC-OS 1×2×1.0 | 1×2×1.0 mm² (7/0.43) | PVC / PVC (OS) | −25…+100 °C | 6.7 | 68 | 50 | TX PVC / PVC Screened Process Cables (−25…+100 °C)
| TX-PVC-PiMF 4×2×1.0 | 4×2×1.0 mm² (7/0.43) | PVC / PVC (PiMF+OS) | −25…+100 °C | 12.8 | 212 | 96 | TX PVC / PVC Screened Process Cables (−25…+100 °C)
| TX-PVC-OS 1×2×1.5 | 1×2×1.5 mm² (7/0.53) | PVC / PVC (OS) | −25…+100 °C | 7.5 | 92 | 56 | TX PVC / PVC Screened Process Cables (−25…+100 °C)
| TX-PVC-PiMF 4×2×1.5 | 4×2×1.5 mm² (7/0.53) | PVC / PVC (PiMF+OS) | −25…+100 °C | 14.3 | 286 | 107 | TX PVC / PVC Screened Process Cables (−25…+100 °C)
| TX-FEP-OS 1×2×0.22 | 1×2×0.22 mm² (7/0.20) | FEP / FEP (OS) | −190…+200 °C | 3.6 | 22 | 27 | TX FEP / FEP Cryogenic & Steam-Autoclave Cables (−190…+200 °C)
| TX-FEP-OS 1×2×0.5 | 1×2×0.5 mm² (7/0.30) | FEP / FEP (OS) | −190…+200 °C | 4.6 | 38 | 34 | TX FEP / FEP Cryogenic & Steam-Autoclave Cables (−190…+200 °C)
| TX-FEP-PiMF 4×2×0.5 | 4×2×0.5 mm² (7/0.30) | FEP / FEP (PiMF+OS) | −190…+200 °C | 9.2 | 128 | 69 | TX FEP / FEP Cryogenic & Steam-Autoclave Cables (−190…+200 °C)
| TX-FEP-OS 1×2×1.0 | 1×2×1.0 mm² (7/0.43) | FEP / FEP (OS) | −190…+200 °C | 5.6 | 58 | 42 | TX FEP / FEP Cryogenic & Steam-Autoclave Cables (−190…+200 °C)
| TX-XLPE-SWA 1×2×1.5 | 1×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | −40…+90 °C | 12.1 | 298 | 121 | TX XLPE / LSZH / SWA Armoured LNG & Cold-Box Cables (−40…+90 °C)
| TX-XLPE-SWA 4×2×1.5 | 4×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | −40…+90 °C | 19.8 | 745 | 198 | TX XLPE / LSZH / SWA Armoured LNG & Cold-Box Cables (−40…+90 °C)
Specify 'IEC' (+ Brown / − White) or 'ANSI' (+ Blue / − Red) colour coding and Class 1 (±0.5 °C) tolerance when ordering.

## Loop resistance & EMF parameter
TX / Type T extension Thermocouple Cable – Loop resistance & EMF parameters by conductor size (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Conductor size | (+) Cu R₂₀ Ω/m ≈ | (−) CuNi R₂₀ Ω/m ≈ | Loop R₂₀ / pair Ω/m ≈ | Class 1 tol. (−25…+100 °C)
0.22 mm² (7/0.20 mm · AWG 24) | 0.082 | 2.23 | 2.31 | ±0.5 °C (±30 µV)
0.50 mm² (7/0.30 mm · AWG 20) | 0.036 | 0.98 | 1.02 | ±0.5 °C (±30 µV)
1.00 mm² (7/0.43 mm · AWG 17) | 0.018 | 0.49 | 0.51 | ±0.5 °C (±30 µV)
1.50 mm² (7/0.53 mm · AWG 16) | 0.012 | 0.33 | 0.34 | ±0.5 °C (±30 µV)
Because the positive leg is high-purity copper (0.018 Ω/m at 1.0 mm²), Type TX has the lowest loop resistance (~0.51 Ω/m) of any base-metal thermocouple extension cable.

## Technical data
TX / Type T extension Thermocouple Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/tx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Alloy pair | Cu (+) / CuNi (Pure Copper (+) / 55Cu45Ni (−))
Key data | EMF tolerance | Class 1: ±0.5 °C (±30 µV · Class 2: ±1.0 °C)
Key data | Loop resistance | ≈ 0.51 Ω/m/pair (at 1.0 mm² (0.018 + 0.49 Ω/m))
Key data | IEC colour code | + Brown / − Wh (Brown outer jacket (or Ex-i Blue))
Key data | ANSI colour code | + Blue / − Red (Blue outer jacket (ASTM E230))
Key data | Temp. range | −190…+200 °C (with FEP/PTFE · −25…+100 °C PVC)
Electrical | Positive conductor (+) | High-purity Copper (Cu, non-magnetic, ~1.72 µΩ·cm)
Electrical | Negative conductor (−) | Copper-Nickel (CuNi ~55 % Cu / 45 % Ni, non-magnetic, ~49 µΩ·cm)
Electrical | Tolerance Class 1 (IEC 60584-3) | ±0.5 °C (±30 µV) over −25 °C to +100 °C junction range
Electrical | Tolerance Class 2 (IEC 60584-3) | ±1.0 °C (±60 µV) over −25 °C to +100 °C junction range
Electrical | Nominal Seebeck coefficient | ≈ 42.8 µV/°C (0 to +100 °C) · loop R ≈ 0.51 Ω/m at 1.0 mm²
Thermal | Standard IEC 60584-3 calibration range | −25 °C to +100 °C (extended −190 °C to +200 °C on FEP sensor-grade)
Thermal | Insulation rating (by jacket type) | −25…+100 °C (PVC) · −40…+90 °C (XLPE/LSZH) · −190…+200 °C (FEP)
Mechanical | Conductor stranding | 0.22 mm² (7/0.20) · 0.5 mm² (7/0.30) · 1.0 mm² (7/0.43) · 1.5 mm² (7/0.53)
Mechanical | Min. bending radius | 7.5 × OD (unarmoured) · 10 × OD (SWA armoured)
Resistance | Flame retardance | IEC 60332-1-2 & IEC 60332-3-24 Cat C (UL 94 V-0 on FEP)
Resistance | Moisture & steam resistance | Non-hygroscopic FEP/PTFE withstands saturated CIP/SIP steam
Standards | Thermocouple cable standard | IEC 60584-3, ANSI/ISA MC96.1 (ASTM E230) & DIN 43722
Standards | Cable construction standard | BS EN 50288-7 / BS 5308
Identification | IEC 60584-3 colour code | (+) Brown · (−) White · Outer sheath: Brown (or Blue Ex-i)
Identification | ANSI MC96.1 colour code | (+) Blue · (−) Red · Outer sheath: Blue
Identification | Customs tariff (HS) | 8544.49

## Construction
TX / Type T extension Thermocouple Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/tx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | True Type TX thermocouple alloy conductors | Positive (+): High-purity oxygen-free Copper (Cu) · Negative (−): Copper-Nickel (CuNi 55/45), both non-magnetic
2 | Colour-coded core insulation | PVC, XLPE, or cryogenic/autoclave FEP/PTFE (IEC: + Brown / − White; ANSI: + Blue / − Red)
3 | Individual & collective Al/PET screens | Aluminium/PET laminated tape + 0.5 mm² tinned copper drain wire (OS or PiMF+OS)
4 | Optional SWA or tinned copper braid | Unarmoured, tinned copper braid screen, or Galvanised Steel Wire Armour (SWA)
5 | Outer jacket (IEC Brown, ANSI Blue or Ex-i Blue) | Flame-retardant PVC, Low-Smoke Zero-Halogen (LSZH), or fluoropolymer FEP/PTFE | IEC 60332-1-2 / IEC 60332-3-24 flame retardant
| TX — IEC 60584-3 (Brown/White) | Positive (+) Brown, Negative (−) White, Outer Jacket Brown
| TX — ANSI MC96.1 (Blue/Red) | Positive (+) Blue, Negative (−) Red, Outer Jacket Blue per ASTM E230
| TX-FEP (Cryogenic / Autoclave) | Extruded FEP/PTFE fluoropolymer rated from −190 °C (cryogenic) to +200 °C (steam autoclave)

## Quality and supply
TX / Type T extension Thermocouple Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/tx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Thermoelectric EMF calibration test (IEC 60584-3 Class 1) — EMF deviation within ±0.5 °C (±30 µV) at +100 °C reference temperature | Every alloy batch
Routine test | 1500 V / 2000 V AC dielectric & continuity test — 1 min AC withstand test without breakdown | Every manufactured drum
Standard / approval | IEC 60584-3 Class 1 (±0.5 °C) Certified
Standard / approval | ANSI/ISA MC96.1 & ASTM E230 Special Limits
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX TX TYPE T EXTENSION <size> IEC 60584-3 CLASS 1 CE
Supply | Delivery form: Non-returnable fumigated wooden drums
Supply | Standard lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP