## Request a quote
Request a quotation for Three-Phase HTS Power Cable
Application engineer · HTS & utility transmission cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/cryogenic-liquid-nitrogen-cooled-tri-axial-three-phase-high-temperature-superconducting-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Three-Phase HTS Power Cable – Architecture, voltage, current, MVA capacity & cryostat OD (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/cryogenic-liquid-nitrogen-cooled-tri-axial-three-phase-high-temperature-superconducting-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 62895 / IEC 61788-26 / IEEE 1726 / CIGRE TB 538. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Design | Voltage · Power | Cryostat Ø mm | Rated I_rms kA | 3-Phase S MVA | Min. bend R mm | Series
| HTS-3P-TriAx-10kV-2.5kA | 3-Phase Concentric REBCO | 10 kV AC · 43 MVA | 125 | 2.5 | 43 | 1800 | Concentric Tri-Axial 3-Phase Medium-Voltage HTS Grid Cables (10 kV to 35 kV)
| HTS-3P-TriAx-10kV-4.0kA | 3-Phase Concentric REBCO | 10 kV AC · 69 MVA | 135 | 4 | 69 | 2000 | Concentric Tri-Axial 3-Phase Medium-Voltage HTS Grid Cables (10 kV to 35 kV)
| HTS-3P-TriAx-24kV-2.5kA | 3-Phase Concentric REBCO | 24 kV AC · 104 MVA | 142 | 2.5 | 104 | 2100 | Concentric Tri-Axial 3-Phase Medium-Voltage HTS Grid Cables (10 kV to 35 kV)
| HTS-3P-TriAx-35kV-3.0kA | 3-Phase Concentric REBCO | 35 kV AC · 182 MVA | 156 | 3 | 182 | 2300 | Concentric Tri-Axial 3-Phase Medium-Voltage HTS Grid Cables (10 kV to 35 kV)
| HTS-3P-3in1-66kV-2.5kA | 3-in-1 Triad REBCO Cores | 66 kV AC · 286 MVA | 168 | 2.5 | 286 | 2500 | 3-in-1 Triad Cold-Dielectric High-Voltage HTS Grid Cables (66 kV to 110 kV)
| HTS-3P-3in1-110kV-3.0kA | 3-in-1 Triad REBCO Cores | 110 kV AC · 572 MVA | 185 | 3 | 572 | 2800 | 3-in-1 Triad Cold-Dielectric High-Voltage HTS Grid Cables (66 kV to 110 kV)
Drum lengths of 300 m to 600 m are joined with low-loss (< 20 nΩ) cryogenic field splices for multi-kilometre routes.

## Technical data
Three-Phase HTS Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/cryogenic-liquid-nitrogen-cooled-tri-axial-three-phase-high-temperature-superconducting-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 62895 / IEC 61788-26 / IEEE 1726 / CIGRE TB 538. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 10 to 110 kV AC (10 / 24 / 35 / 66 / 110 kV grid)
Key data | Phase current | 2.0 to 4.0 kA (43 MVA to 572 MVA in 1 duct)
Key data | Architecture | Tri-Axial / 3in1 (concentric L1/L2/L3 + Cu screen)
Key data | Cryogen | Subcooled LN₂ (67–77 K at 0.3–1.5 MPa pressure)
Key data | Dielectric | Lapped PPLP (LN₂-impregnated polypropylene)
Key data | Cryostat OD | 125 to 185 mm (double corrugated 316L + MLI)
Electrical | Rated system voltage (U₀/U) & BIL | 6/10 kV (75 kV BIL) · 14/24 kV (125 kV) · 20/35 kV (170 kV) · 64/110 kV
Electrical | Continuous 3-phase AC current & power | 2,000 A to 4,000 A rms (43 MVA at 10 kV up to 572 MVA at 110 kV)
Electrical | Rated short-circuit fault current | 25 kA to 40 kA symmetrical for 0.5–1.0 s (carried by parallel Cu
Electrical | 50/60 Hz AC cryogenic loss | < 0.5 to 1.2 W/m per phase at rated current
Thermal | Subcooled liquid nitrogen (LN₂) window | 67 K inlet to 77 K outlet at 0.3 to 1.5 MPa (prevents nitrogen bubble
Thermal | Thermal cycling & overload stability | Verified thermal ageing and short-circuit withstand per standard
Mechanical | Overall outer diameter (including PE | 125 mm (10 kV Tri-Axial) to 185 mm (110 kV Triad)
Mechanical | Minimum installation bending radius | 1.8 m to 2.8 m (15 × cryostat OD) on Ø 4.2 m transport drums
Resistance | External stray magnetic field (EMF) | Virtually zero (0 µT at 1 m) due to concentric Tri-Axial / HTS-shielded
Resistance | Environmental & chemical durability | Resistant to moisture, industrial fluids and service ageing
Standards | Governing HTS grid cable standards | IEC 62895 (HVDC/AC HTS), IEEE 1726, IEC 61788-26 & CIGRE TB 538
Standards | Factory QA & material compliance | EN 10204 3.1 routine test certificate · RoHS 2 & REACH compliant
Identification | System scope | Supplied with outdoor/indoor LN₂ HV terminations, field splice joints &
Identification | Customs tariff (HS) | 8544.60

## Construction
Three-Phase HTS Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/cryogenic-liquid-nitrogen-cooled-tri-axial-three-phase-high-temperature-superconducting-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 62895 / IEC 61788-26 / IEEE 1726 / CIGRE TB 538. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Concentric Phase L1, L2 & L3 REBCO 2G HTS tape layers | Helically wound 4 mm wide REBCO 2G HTS coated-conductor tapes with matched pitch angles
2 | Central hollow corrugated stainless-steel LN₂ former + | Spiral corrugated AISI 304L/316L tube (ID 35–45 mm) + stranded copper fault-current
3 | Lapped Polypropylene Laminated Paper (PPLP) cryogenic | Multi-layer lapped PPLP tapes impregnated under pressure by subcooled liquid nitrogen
4 | Concentric copper neutral / earth fault screen | Helical copper tapes over outer PPLP dielectric
5 | Double corrugated AISI 316L vacuum-superinsulated | Inner LN₂ containment pipe + 30–50 layers vacuum MLI (< 10⁻⁵ mbar) + outer corrugated
| Concentric Tri-Axial 3-Phase HTS (10 kV to 35 kV · 2.5–4.0 kA) | All three phases wound concentrically on one former — smallest OD and lowest HTS tape usage
| 3-in-1 Triad Cold-Dielectric HTS (66 kV to 110 kV · 2.5–3.0 kA) | Three individually HTS-shielded cores cabled inside a common LN₂ cryostat for HV grid voltages

## Quality and supply
Three-Phase HTS Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/cryogenic-liquid-nitrogen-cooled-tri-axial-three-phase-high-temperature-superconducting-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 62895 / IEC 61788-26 / IEEE 1726 / CIGRE TB 538. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Type test | CIGRE TB 538 / IEC 62895 20-cycle load-cycling, HV AC & lightning impulse test in LN₂ — Zero partial discharge (≤ 5 pC) before and after 15 × OD bending & fault-current shots | Cable + termination + joint system
Routine test | Cryostat helium mass-spectrometer vacuum test (< 10⁻⁵ mbar) & 77 K I_c test — 100 % vacuum integrity and critical current margin verified on drum | Every drum length
Standard / approval | IEC 62895 & IEEE 1726 HTS Transmission Compliant
Standard / approval | CIGRE TB 538 Pre-Qualification Tested
Standard / approval | ISO 21013 Vacuum-Insulated Cryostat Certified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | Embossed on outer PE jacket: TEBAOFLEX 3-PHASE HTS CABLE <kV> <kA> LN2 CRYOGENIC HIGH VOLTAGE
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP