## Request a quote
Request a quotation for TraceTek TT3000
Application engineer · instrumentation & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/tracetek-tt3000-acid-base-and-corrosive-chemical-leak-detection-sensing-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
TraceTek TT3000 Acid, Base and Corrosive Chemical Leak Detection – Dimensions & chemical response (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt3000-acid-base-and-corrosive-chemical-leak-detection-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SEMI S2 / NFPA 262 / UL 910. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Supply format & connectors | Outer Ø mm | Weight ≈ kg/km | Sense R Ω/m | H₂SO₄ Resp. sec | Series
| TraceTek TT3000 (Bulk) | Bulk Reel (50 m / 100 m / 250 m) for Pipe Pull-In | 7 | 44 | 20 | 12 | 4-Wire All-Fluoropolymer Acid & Chemical Leak Sensing Cables
| TraceTek TT3000-PC | Modular Plastic-Connector Lengths (1.5 m to 30 m) | 7 | 44 | 20 | 12 | 4-Wire All-Fluoropolymer Acid & Chemical Leak Sensing Cables
| TraceTek TT3000-MC | Modular Metal-Collar Lengths for Mild Indoor Zones | 7 | 44 | 20 | 12 | 4-Wire All-Fluoropolymer Acid & Chemical Leak Sensing Cables
For outdoor sunlit pipe racks carrying 98 % H₂SO₄ or fuming HNO₃/HF, see UV-stabilized TraceTek TT7000-HUV.

## Technical data
TraceTek TT3000 Acid, Base and Corrosive Chemical Leak Detection – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt3000-acid-base-and-corrosive-chemical-leak-detection-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SEMI S2 / NFPA 262 / UL 910. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Target fluids | Acids, bases, sa (H₂SO₄, HCl, HF, HNO₃, NaOH)
Key data | Wetted material | Fluoropolymer (ECTFE / FEP / PTFE + carbon)
Key data | Outer diameter | 7.0 mm (0.28 in) (With fluoropolymer wicking braid)
Key data | Sensor resistance | ≈ 20.0 Ω/m (±0.5 % leak distance accuracy)
Key data | Operating temp. | -20 to +85 °C (Continuous chemical containment)
Key data | Fire rating | NFPA 262 / UL 91 (Cleanroom & plenum safe)
Electrical | Sensing wire linear R | ≈ 20.0 Ω/m (±2 % linearity for ±0.5 % distance accuracy)
Electrical | Dry insulation resistance | ≥ 100 MΩ per 30 m sensing loop
Electrical | Alarm response time | < 5 s (10 % HCl / NaOH) · < 15 s (98 % concentrated H₂SO₄)
Electrical | Controller compatibility | All 4-wire 20 Ω/m locating modules (TTSIM, TTDM-128, PLC)
Thermal | Continuous operating temp. | -20 °C to +85 °C
Thermal | Short-term washdown peak | +100 °C
Thermal | Plenum fire rating | NFPA 262 / UL 910 low-smoke plenum qualified
Mechanical | Nominal outer diameter | 7.0 mm (0.28 in)
Mechanical | Min. bend radius | 30 mm (4.5 × OD)
Mechanical | Pulling tension (pipe) | Up to 130 N (30 lbf) for pulling through interstitial containment pipes
Resistance | Acid resistance | 98 % H₂SO₄, 37 % HCl, 49 % HF, 70 % HNO₃, 85 % H₃PO₄, Aqua Regia
Resistance | Alkali & oxidizer resist. | 50 % NaOH, 45 % KOH, 29 % NH₄OH, 30 % H₂O₂, 15 % NaOCl bleach
Resistance | Reusability after spill | Flush with DI water and dry to restore full baseline IR
Standards | Semiconductor safety | SEMI S2 & SEMI S6 liquid chemical leak containment
Standards | Fire & hazardous location | NFPA 262 Plenum · Intrinsically Safe (Ex ia) with zener barrier
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Visual identification | Green fluoropolymer core visible through translucent/green wicking braid
Identification | Customs tariff (HS) | 8544.4290
Identification | Connector system | Acid-resistant non-metallic threaded/snap TraceTek connectors

## Construction
TraceTek TT3000 Acid, Base and Corrosive Chemical Leak Detection – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt3000-acid-base-and-corrosive-chemical-leak-detection-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SEMI S2 / NFPA 262 / UL 910. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 2 × fluoropolymer-insulated copper reference wires | 2 × 26 AWG stranded tinned/nickel copper conductors with pinhole-free fluoropolymer primary insulation
2 | Fluted green fluoropolymer central support core | Chemically inert perfluorinated/fluoropolymer central spline maintaining exact 4-wire helical geometry
3 | 2 × carbon-fluoropolymer chemical sensing electrodes | 2 × conductive-fluoropolymer jacketed sensing wires calibrated to ~20.0 Ω/m linear resistance
4 | Capillary-wicking fluoropolymer outer overbraid | Specially treated open-weave fluoropolymer monofilament braid (distinctive Green/Black tracer)
| TraceTek TT3000 (Bulk Reel) | 7.0 mm OD all-fluoropolymer acid/base leak sensing cable for pull-in double-containment pipes & trenches
| TraceTek TT3000-PC (Modular Plastic Connector) | Pre-terminated TT3000 sensor lengths (1.5 m to 30 m) with acid-resistant fluoropolymer/plastic connectors

## Quality and supply
TraceTek TT3000 Acid, Base and Corrosive Chemical Leak Detection – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt3000-acid-base-and-corrosive-chemical-leak-detection-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SEMI S2 / NFPA 262 / UL 910. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % linear resistance (20.0 Ω/m) & 4-wire continuity test — Resistance gradient within ±2 % and dry IR ≥ 100 MΩ | Every manufactured reel / assembly
Type test | Concentrated acid & alkali immersion / reset cycle test — Survives 98 % H₂SO₄, 49 % HF, 37 % HCl & 50 % NaOH with full DI-rinse recovery | Qualification test
Type test | NFPA 262 (UL 910) plenum flame & smoke test — Approved for cleanroom sub-fab air plenums | Qualification test
Standard / approval | SEMI S2 Sub-Fab Compliant
Standard / approval | NFPA 262 / UL 910 Plenum
Standard / approval | Ex ia Intrinsically Safe Simple Apparatus
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | Tag & connector print: TEBAOFLEX TRACETEK TT3000 ACID/CHEMICAL
Supply | Delivery form: Fumigated wooden drums, steel reels or precision spools
Supply | Standard lengths: 500 m · 1000 m (or custom cut/spooled lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP