## Request a quote
Request a quotation for TraceTek TT5000
Application engineer · instrumentation & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/tracetek-tt5000-hydrocarbon-fuel-and-solvent-leak-detection-sensing-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
TraceTek TT5000 Hydrocarbon Fuel and Solvent Leak Detection – Dimensions & hydrocarbon response (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt5000-hydrocarbon-fuel-and-solvent-leak-detection-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 913 / IEC 60079-11 / EPA 40 CFR 280. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Supply format & duty | Body Ø mm | Weight ≈ kg/km | Jet/Petrol min | #2 Diesel min | Series
| TraceTek TT5000 (Bulk) | Bulk Reel for Slotted Conduit & Pipe Pull-In | 9.5 | 88 | 5 | 30 | 4-Wire Swelling-Polymer Hydrocarbon Fuel Sensing Cables
| TraceTek TT5000-PC | Modular Plastic Connectors (1.5 m to 15 m) · Wet Sumps | 9.5 | 88 | 5 | 30 | 4-Wire Swelling-Polymer Hydrocarbon Fuel Sensing Cables
| TraceTek TT5000-MC | Modular Metal Connectors · Indoor Generator Rooms | 9.5 | 88 | 5 | 30 | 4-Wire Swelling-Polymer Hydrocarbon Fuel Sensing Cables
For ultra-fast response (< 1–3 min) to light organic solvents (MEK, acetone, benzene, toluene), see TraceTek TT5001 / TT5001-HUV.

## Technical data
TraceTek TT5000 Hydrocarbon Fuel and Solvent Leak Detection – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt5000-hydrocarbon-fuel-and-solvent-leak-detection-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 913 / IEC 60079-11 / EPA 40 CFR 280. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Selectivity | Fuel only (No H₂ (Ignores rain & groundwater)
Key data | Target fluids | Jet, diesel, pet (Kerosene, crude, biodiesel, BTX)
Key data | Outer diameter | 9.0 to 10.5 mm (With protective outer braid)
Key data | Sensor resistance | ≈ 20.0 Ω/m (Standard 4-wire locating loop)
Key data | Ex classification | Ex ia IIC T4 Ga (Simple apparatus with barrier)
Key data | Operating temp. | -20 to +60 °C (Fuel containment trenches/pipes)
Electrical | Sensing wire linear R | ≈ 20.0 Ω/m (±2 % linearity — uses standard TTDM/TTSIM modules)
Electrical | Dry / water-immersed IR | ≥ 100 MΩ in dry air or clean tap/rainwater
Electrical | Location accuracy | ± 0.5 % of total sensing circuit length
Electrical | Intrinsic safety rating | Ex ia IIC T4 Ga (Simple Apparatus per IEC 60079-11 Cl. 5.7)
Thermal | Continuous operating temp. | -20 °C to +60 °C
Thermal | Storage temperature | -30 °C to +70 °C
Thermal | Response time @ 20 °C | ≈ 3–8 min (Gasoline / Jet A-1) · ≈ 15–45 min (#2 Diesel)
Mechanical | Nominal outer diameter | 9.5 mm (cable body) · 14–19 mm (at modular connector)
Mechanical | Min. bend radius | 50 mm (5 × OD)
Mechanical | Max. pulling tension | 220 N (50 lbf)
Resistance | Detected hydrocarbons | Gasoline, Jet A / JP-8, #1/#2 Diesel, Kerosene, Toluene, Xylene
Resistance | Water & methane immunity | Does not alarm in liquid water or gaseous methane/natural gas
Resistance | Volatile fuel recovery | Can reset after light gasoline/solvent evaporation (replace after heavy diesel saturation)
Standards | UST leak detection | US EPA 40 CFR Part 280 & NWGLDE Third-Party Listed
Standards | Hazardous locations | UL 913 / FM Class I Div 1 & ATEX/IECEx Zone 0 (with barrier)
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Visual identification | Black outer braid with Yellow tracer & fuel warning tag
Identification | Customs tariff (HS) | 8544.4290
Identification | System compatibility | Mix-and-match on same 4-wire loop with TT1000 / TT3000 / TT5001

## Construction
TraceTek TT5000 Hydrocarbon Fuel and Solvent Leak Detection – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt5000-hydrocarbon-fuel-and-solvent-leak-detection-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 913 / IEC 60079-11 / EPA 40 CFR 280. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 2 × insulated copper reference & continuity wires | 2 × 26 AWG stranded tinned copper conductors with fuel-proof fluoropolymer insulation
2 | Inner conductive-polymer sensing electrode + spacer | Inner calibrated conductive-polymer electrode (~20.0 Ω/m) separated from the outer sensing wire by an open helical gap
3 | Hydrocarbon-absorbent swelling elastomer actuator | Proprietary cross-linked organosilicone/elastomer matrix that swells rapidly upon absorbing liquid hydrocarbons
4 | Protective high-tenacity polymer outer braid | Abrasion-resistant Black/Yellow woven fluoropolymer/polyester outer braid (nominal 9.5–10.5 mm OD)
| TraceTek TT5000 (Bulk Reel) | Bulk hydrocarbon fuel sensing cable for pulling into containment conduits and pipeline trenches
| TraceTek TT5000-MC / TT5000-PC (Modular) | Pre-terminated modular lengths (1.5 m, 3 m, 7.5 m, 15 m) with metal or plastic connectors for generator pans

## Quality and supply
TraceTek TT5000 Hydrocarbon Fuel and Solvent Leak Detection – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt5000-hydrocarbon-fuel-and-solvent-leak-detection-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 913 / IEC 60079-11 / EPA 40 CFR 280. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % linear sensing resistance (20.0 Ω/m) & dry IR test — 20.0 Ω/m ± 2 % and open-circuit IR ≥ 100 MΩ | Every manufactured reel / assembly
Type test | EPA / NWGLDE water-immersion + floating hydrocarbon sheen test — Zero false alarm in water; positive alarm & location on 3 mm fuel layer | Qualification test
Sample test | Iso-octane / Jet A-1 / #2 Diesel response time verification — Meets batch swelling actuation time limits | Per production lot
Standard / approval | EPA 40 CFR 280 / NWGLDE
Standard / approval | Ex ia IIC Simple Apparatus
Standard / approval | CE, RoHS 2 & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | Tag & connector print: TEBAOFLEX TRACETEK TT5000 FUEL/SOLVENT
Supply | Delivery form: Fumigated wooden drums, steel reels or precision spools
Supply | Standard lengths: 500 m · 1000 m (or custom cut/spooled lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP