## Request a quote
Request a quotation for TraceTek TT7000-HUV
Application engineer · instrumentation & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/tracetek-tt7000-huv-uv-stabilized-outdoor-aggressive-acid-leak-sensing-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
TraceTek TT7000-HUV UV-Stabilized Outdoor Aggressive Acid Leak – Dimensions & acid sensing ratings (2)
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt7000-huv-uv-stabilized-outdoor-aggressive-acid-leak-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SEMI S2 / IEC 60079-11 / ISO 4892. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Supply format & connectors | Outer Ø mm | Weight ≈ kg/km | Max. temp. °C | 98% H₂SO₄ sec | Series
| TraceTek TT7000-HUV (Bulk) | Bulk Reel (50 m / 100 m / 250 m) · Outdoor Acid Racks | 7.5 | 56 | 120 | 10 | UV-Stabilized Perfluorinated Aggressive Acid Leak Sensing Cables
| TraceTek TT7000-HUV-PC | Modular UV-Black Acid-Proof Connector Lengths | 7.5 | 56 | 120 | 10 | UV-Stabilized Perfluorinated Aggressive Acid Leak Sensing Cables
Uses the same 20.0 Ω/m 4-wire resistance gradient as TT1000 and TT3000 for seamless integration with TTSIM and TTDM-128 panels.

## Technical data
TraceTek TT7000-HUV UV-Stabilized Outdoor Aggressive Acid Leak – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt7000-huv-uv-stabilized-outdoor-aggressive-acid-leak-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SEMI S2 / IEC 60079-11 / ISO 4892. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Target fluids | Aggressive acids (98% H₂SO₄, fuming HNO₃, HF, HCl)
Key data | Wetted polymer | Perfluorinated (PFA / PTFE + carbon black)
Key data | Outer diameter | 7.5 mm (0.30 in) (Heavy-duty UV porous braid)
Key data | Sensor resistance | ≈ 20.0 Ω/m (±0.5 % leak distance accuracy)
Key data | Operating temp. | -40 to +120 °C (Highest thermal rating in series)
Key data | UV weathering | Full outdoor sun (Carbon-black UV fluoropolymer)
Electrical | Sensing wire linear R | ≈ 20.0 Ω/m (±2 % linearity — works with all TraceTek modules)
Electrical | Dry insulation resistance | ≥ 100 MΩ per 30 m sensing loop
Electrical | Response time (98 % H₂SO₄) | < 10 seconds upon contact with microporous braid
Electrical | Hazardous area rating | Ex ia IIC T4 Ga Simple Apparatus (with zener barrier)
Thermal | Continuous operating temp. | -40 °C to +120 °C (+248 °F)
Thermal | Short-term steam/acid peak | +140 °C
Thermal | Cold impact temperature | -40 °C outdoor arctic tank-farm service
Mechanical | Nominal outer diameter | 7.5 mm (0.30 in)
Mechanical | Min. bend radius | 35 mm (4.5 × OD)
Mechanical | Max. pulling tension | 180 N (40 lbf)
Resistance | Extreme acid resistance | 98 % H₂SO₄, Oleum, 70–90 % Fuming HNO₃, 49 % HF, Aqua Regia
Resistance | Solar UV weathering | Carbon-black UV fluoropolymer braid per ISO 4892 / ASTM G154
Resistance | Decontamination & reuse | Neutralize, flush with clean water and dry to reset
Standards | Explosion protection | IEC 60079-11 / UL 913 Intrinsically Safe Simple Apparatus
Standards | Chemical containment | SEMI S2 & EPA RCRA hazardous chemical secondary containment
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Visual identification | Matte Black UV microporous fluoropolymer braid with Red/Black acid tag
Identification | Customs tariff (HS) | 8544.4290
Identification | Connector system | UV-Black perfluorinated/acid-resistant non-metallic connectors (-PC)

## Construction
TraceTek TT7000-HUV UV-Stabilized Outdoor Aggressive Acid Leak – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt7000-huv-uv-stabilized-outdoor-aggressive-acid-leak-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SEMI S2 / IEC 60079-11 / ISO 4892. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 2 × PFA-insulated nickel/tinned copper reference wires | 2 × 26 AWG stranded nickel/tinned copper conductors with thick-wall Perfluoroalkoxy (PFA) primary insulation | Prevents acid vapor permeation up to +120 °C
2 | Perfluorinated high-temperature fluted central spline | Extruded PFA/PTFE fluted carrier rod locking all 4 helical conductors against crush and thermal expansion
3 | 2 × carbon-PFA conductive sensing electrodes | 2 × perfluorinated conductive-polymer sensing wires calibrated to ~20.0 Ω/m linear resistance
4 | UV-stabilized microporous fluoropolymer outer braid | Carbon-black pigmented microporous PTFE/PFA woven outer jacket (nominal 7.5 mm OD)
| TraceTek TT7000-HUV (Bulk Reel) | 7.5 mm OD UV-stabilized perfluorinated aggressive acid sensing cable in bulk pull-in reels
| TraceTek TT7000-HUV-PC (Modular) | Pre-terminated modular lengths (1.5 m to 15 m) with UV-black acid-proof fluoropolymer connectors

## Quality and supply
TraceTek TT7000-HUV UV-Stabilized Outdoor Aggressive Acid Leak – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/tracetek-tt7000-huv-uv-stabilized-outdoor-aggressive-acid-leak-sensing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SEMI S2 / IEC 60079-11 / ISO 4892. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % linear sensing resistance (20.0 Ω/m) & dry IR check — 20.0 Ω/m ± 2 % and dry open-circuit IR ≥ 100 MΩ | Every manufactured reel / assembly
Type test | 98 % H₂SO₄, 70 % HNO₃ & 49 % HF elevated-temperature immersion test — Zero polymer cracking or resistance drift after +90 °C acid immersion | Qualification test
Type test | ISO 4892 / ASTM G154 Xenon-arc solar UV weathering test — Retains ≥ 90 % tensile strength and wicking speed after 3,000 h UV | Qualification test
Standard / approval | Ex ia IIC Simple Apparatus
Standard / approval | ISO 4892 Outdoor UV
Standard / approval | SEMI S2 & RoHS 2
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | Tag & connector print: TEBAOFLEX TRACETEK TT7000-HUV AGGRESSIVE ACID
Supply | Delivery form: Fumigated wooden drums, steel reels or precision spools
Supply | Standard lengths: 500 m · 1000 m (or custom cut/spooled lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP