## Request a quote
Request a quotation for Type G-GC
Application engineer · North American mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-g-gc-cable-icea-nema-msha/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Type G-GC 2 kV Portable Mining Power Cable – Sizes & dimensions · 2 kV (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-g-gc-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Power cores 3 × AWG/kcmil | Phase strands | Grounds (2) AWG (strands) | Pilot (GC) AWG | Insulation mils | Insulation mm | Nominal OD in | Nominal OD mm | Weight ≈ lb/kft | Mass ≈ kg/km | Ampacity A (40 °C)
| Type G-GC · 3 × 8 AWG | 133 | 2 × 10 (49) | 10 | 60 | 1.52 | 0.97 | 24.6 | 600 | 893 | 59
| Type G-GC · 3 × 6 AWG | 259 | 2 × 10 (49) | 10 | 60 | 1.52 | 1.05 | 26.7 | 750 | 1116 | 79
| Type G-GC · 3 × 4 AWG | 259 | 2 × 8 (133) | 10 | 60 | 1.52 | 1.19 | 30.2 | 1070 | 1592 | 104
| Type G-GC · 3 × 2 AWG | 259 | 2 × 7 (133) | 10 | 60 | 1.52 | 1.34 | 34 | 1480 | 2202 | 138
| Type G-GC · 3 × 1 AWG | 259 | 2 × 6 (133) | 8 | 80 | 2.03 | 1.51 | 38.4 | 1890 | 2813 | 161
| Type G-GC · 3 × 1/0 AWG | 266 | 2 × 5 (133) | 8 | 80 | 2.03 | 1.65 | 41.9 | 2340 | 3482 | 186
| Type G-GC · 3 × 2/0 AWG | 323 | 2 × 4 (259) | 8 | 80 | 2.03 | 1.75 | 44.5 | 2750 | 4092 | 215
| Type G-GC · 3 × 3/0 AWG | 418 | 2 × 2 (259) | 8 | 80 | 2.03 | 1.89 | 48 | 3377 | 5026 | 249
| Type G-GC · 3 × 4/0 AWG | 532 | 2 × 2 (259) | 8 | 80 | 2.03 | 2.04 | 51.8 | 3980 | 5923 | 287
| Type G-GC · 3 × 250 kcmil | 627 | 2 × 2 (259) | 6 | 95 | 2.41 | 2.39 | 60.7 | 5000 | 7441 | 320
| Type G-GC · 3 × 350 kcmil | 888 | 2 × 1/0 (266) | 6 | 95 | 2.41 | 2.68 | 68.1 | 6750 | 10046 | 394
| Type G-GC · 3 × 500 kcmil | 1221 | 2 × 2/0 (323) | 6 | 95 | 2.41 | 3.03 | 77 | 8900 | 13245 | 487
Ampacity based on 90 °C conductor temperature at 40 °C ambient in free air (single cable) per ICEA S-75-381.
3 × 3 AWG (between 4 AWG and 2 AWG) is also available on request.

## Technical data
Type G-GC 2 kV Portable Mining Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-g-gc-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 2,000 V (Three-phase AC / DC mining power)
Key data | Core arrangement | 3P + 2G + 1GC (3 phase + 2 ground + 1 pilot)
Key data | Size range | 8 AWG–500 kcmil (12 standard sizes · 59–487 A)
Key data | Max. conductor T | +90 °C (Dry & wet · 130 °C overload)
Key data | Min. operating T | −40 °C (Cold-bend & impact rated)
Key data | Min. bend radius | 6 × OD (≤ 2 in OD; 8 × OD above)
Electrical | Rated voltage | 2,000 V (phase-to-phase)
Electrical | Ampacity range | 59 to 487 A (90 °C conductor, 40 °C ambient in free air)
Electrical | Grounding conductors | Two symmetrically split green-insulated or bare tinned copper grounds (≥ 50 % of one phase conductor total area)
Electrical | Ground-check pilot | One yellow-insulated tinned copper pilot (10, 8 or 6 AWG) for fail-safe continuity monitoring
Electrical | Shielding | Unshielded (specify Type SHD-GC when metallic phase shielding is required)
Thermal | Max. continuous conductor temp. | +90 °C (dry / wet)
Thermal | Min. operating temperature | −40 °C
Thermal | Emergency overload temperature | +130 °C
Thermal | Short-circuit temperature | +250 °C
Mechanical | Min. bending radius | 6 × OD (≤ 2.0 in / 50.8 mm OD); 8 × OD (> 2.0 in OD)
Mechanical | Phase conductor stranding | Rope-lay stranded annealed tinned copper (133 to 1,221 strands)
Mechanical | Jacket reinforcement | Two-layer extra-heavy-duty CPE jacket with integral reinforcing cord
Resistance | Flame retardance | MSHA 30 CFR Part 7 flame test;CSA FT4
Resistance | Oil, abrasion & impact | Heavy-duty CPE resists cutting, rock impact, oil, grease, acids and alkalis
Resistance | Water & sunlight | 90 °C wet/dry rated; UV and weather resistant black jacket
Standards | Construction standard | ICEA S-75-381 / NEMA WC 58
Standards | Conductor standard | ASTM B172 / ASTM B33 (rope-lay tinned copper)
Standards | Mine safety & flame | MSHA 30 CFR Part 7; CSA C22.2 No. 96
Identification | Phase core colours | Black, White, Red
Identification | Ground & ground-check identification | Grounds: 2 × Green (or uninsulated tinned copper) · Ground-check: 1 × Yellow
Identification | Outer jacket | Black heavy-duty thermoset CPE (custom colours on request)

## Construction
Type G-GC 2 kV Portable Mining Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-g-gc-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase conductors (3) | Rope-lay stranded annealed tinned copper | ASTM B172 / ASTM B33
2 | Separator tape | Polyester separator tape over phase conductors
3 | Phase insulation | 90 °C EPR (ethylene propylene rubber), Black, White, Red | ICEA S-75-381 Part 3
4 | Grounding conductors (2) | Two green-insulated or bare rope-lay tinned copper grounds in two interstices | Combined area ≥ 50 % of one phase core
5 | Ground-check pilot (1) | One yellow EPR/PP-insulated tinned copper pilot (10, 8 or 6 AWG) in third interstice
6 | Reinforcing binder | Open-weave synthetic reinforcing cord between inner and outer jacket layers
7 | Outer jacket | Two-layer extra-heavy-duty thermoset CPE (chlorinated polyethylene), black | ICEA S-75-381 / MSHA
| Phase cores (3) | Black, White, Red 90 °C EPR insulation (60 to 95 mils radial wall)
| Interstitial grounds (2) + pilot (1) | Two split green grounds plus one yellow ground-check conductor (10, 8 or 6 AWG)

## Quality and supply
Type G-GC 2 kV Portable Mining Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-g-gc-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | In-line spark test of phase & ground-check cores — 100 % high-voltage AC spark test before cabling | Every core
Routine test | Conductor & pilot DC resistance + AC high-voltage test — Verified on all 3 phase cores, 2 grounds and 1 ground-check pilot per ICEA S-75-381 | Every shipping length
Sample test | Vertical flame resistance test — Self-extinguishing per MSHA 30 CFR Part 7 / CSA FT4 | Production batch
Sample test | Laser diameter & sheath concentricity — Minimum wall thickness and nominal OD verification | Every drum
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · TYPE G-GC · 2000V · 90C · 3/C [size] · EPR/CPE · ICEA S-75-381 · FT4
Supply | Delivery form: Export seaworthy fumigated wooden drums matched to cable bend radius
Supply | Lengths: Custom cut-to-length reels per machine circuit schedule
Supply | Certificate: EN 10204 3.1 inspection certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None