## Request a quote
Request a quotation for Type G
Application engineer · North American mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-g-cable-icea-nema-msha/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Type G Portable Mining Power Cable (ICEA/NEMA/MSHA) – Flat 2C + Ground · 600–2,000 V (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-g-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Configuration · size | Power strands | Ground conductor | Insulation in | Insulation mm | Height H mm | Width W mm | H × W in | Weight ≈ lb/kft | Mass ≈ kg/km | Ampacity A (40 °C)
| Type G Flat · 2 × 8 AWG + G | 133 (7×19) | 1 × 8 AWG | 0.06 | 1.5 | 13 | 21.3 | 0.51 × 0.84 | 340 | 505 | 72
| Type G Flat · 2 × 6 AWG + G | 133 (7×19) | 1 × 8 AWG | 0.06 | 1.5 | 14.2 | 23.6 | 0.56 × 0.93 | 440 | 655 | 95
| Type G Flat · 2 × 4 AWG + G | 259 (7×37) | 1 × 6 AWG | 0.06 | 1.5 | 15.5 | 26.7 | 0.61 × 1.05 | 580 | 863 | 127
| Type G Flat · 2 × 2 AWG + G | 259 (7×37) | 1 × 5 AWG | 0.06 | 1.5 | 18.5 | 31.5 | 0.73 × 1.24 | 850 | 1265 | 167
| Type G Flat · 2 × 1 AWG + G | 259 (7×37) | 1 × 4 AWG | 0.08 | 2 | 20.6 | 35.6 | 0.81 × 1.40 | 1070 | 1592 | 191
| Type G Flat · 2 × 1/0 AWG + G | 259 (7×37) | 1 × 3 AWG | 0.08 | 2 | 23.6 | 38.4 | 0.93 × 1.51 | 1310 | 1949 | 217
| Type G Flat · 2 × 2/0 AWG + G | 329 (7×47) | 1 × 2 AWG | 0.08 | 2 | 25.1 | 41.4 | 0.99 × 1.63 | 1600 | 2381 | 250
| Type G Flat · 2 × 4/0 AWG + G | 532 (19×28) | 1 × 1/0 AWG | 0.08 | 2 | 27.9 | 48 | 1.10 × 1.89 | 2300 | 3423 | 328
Paired H × W values indicate nominal minor height × major width in inches and millimetres.
Ampacity based on 90 °C conductor temperature at 40 °C ambient in free air.

## Round 3C & 4C · 2,000 V
Type G Portable Mining Power Cable (ICEA/NEMA/MSHA) – Round 3C & 4C · 2,000 V (24)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-g-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
Configuration · size | Phase strands | Grounds count × AWG | Insulation mils | Insulation mm | Nominal OD in | Nominal OD mm | Weight ≈ lb/kft | Mass ≈ kg/km | Ampacity A (40 °C) | Series
Type G Round · 3 × 8 AWG | 133 | 3 × 10 AWG | 60 | 1.52 | 0.97 | 24.6 | 595 | 885 | 59 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 6 AWG | 259 | 3 × 10 AWG | 60 | 1.52 | 1.05 | 26.7 | 745 | 1109 | 79 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 4 AWG | 259 | 3 × 10 AWG | 60 | 1.52 | 1.19 | 30.2 | 1050 | 1563 | 104 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 2 AWG | 259 | 3 × 9 AWG | 60 | 1.52 | 1.34 | 34 | 1460 | 2173 | 138 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 1 AWG | 259 | 3 × 8 AWG | 80 | 2.03 | 1.51 | 38.4 | 1880 | 2798 | 161 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 1/0 AWG | 266 | 3 × 7 AWG | 80 | 2.03 | 1.65 | 41.9 | 2320 | 3453 | 186 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 2/0 AWG | 323 | 3 × 6 AWG | 80 | 2.03 | 1.75 | 44.5 | 2730 | 4063 | 215 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 3/0 AWG | 418 | 3 × 5 AWG | 80 | 2.03 | 1.89 | 48 | 3350 | 4985 | 249 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 4/0 AWG | 532 | 3 × 4 AWG | 80 | 2.03 | 2.04 | 51.8 | 3950 | 5878 | 287 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 250 kcmil | 627 | 3 × 3 AWG | 95 | 2.41 | 2.39 | 60.7 | 4960 | 7381 | 320 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 350 kcmil | 888 | 3 × 2 AWG | 95 | 2.41 | 2.68 | 68.1 | 6700 | 9971 | 394 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 3 × 500 kcmil | 1221 | 3 × 1/0 AWG | 95 | 2.41 | 3.03 | 77 | 8850 | 13170 | 487 | Type G Round 3C · 2,000 V (3 Power + 3 Interstitial Grounds)
Type G Round · 4 × 8 AWG | 133 | 4 × 12 AWG | 60 | 1.52 | 1.05 | 26.7 | 720 | 1071 | 54 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 6 AWG | 259 | 4 × 12 AWG | 60 | 1.52 | 1.15 | 29.2 | 920 | 1369 | 72 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 4 AWG | 259 | 4 × 10 AWG | 60 | 1.52 | 1.29 | 32.8 | 1290 | 1920 | 93 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 2 AWG | 259 | 4 × 9 AWG | 60 | 1.52 | 1.46 | 37.1 | 1820 | 2708 | 122 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 1 AWG | 259 | 4 × 8 AWG | 80 | 2.03 | 1.69 | 42.9 | 2360 | 3512 | 143 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 1/0 AWG | 266 | 4 × 7 AWG | 80 | 2.03 | 1.84 | 46.7 | 2900 | 4316 | 165 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 2/0 AWG | 323 | 4 × 6 AWG | 80 | 2.03 | 1.98 | 50.3 | 3480 | 5179 | 192 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 3/0 AWG | 418 | 4 × 5 AWG | 80 | 2.03 | 2.13 | 54.1 | 4150 | 6176 | 221 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 4/0 AWG | 532 | 4 × 4 AWG | 80 | 2.03 | 2.31 | 58.7 | 4950 | 7366 | 255 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 250 kcmil | 627 | 4 × 3 AWG | 95 | 2.41 | 2.66 | 67.6 | 6180 | 9197 | 280 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 350 kcmil | 888 | 4 × 2 AWG | 95 | 2.41 | 2.98 | 75.7 | 8300 | 12352 | 335 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Type G Round · 4 × 500 kcmil | 1221 | 4 × 1/0 AWG | 95 | 2.41 | 3.4 | 86.4 | 11050 | 16444 | 395 | Type G Round 4C · 2,000 V (4 Power + 4 Interstitial Grounds)
Round Type G cables distribute 3 (in 3C) or 4 (in 4C) grounding conductors symmetrically in all outer interstices and omit the ground-check pilot.
Where a yellow ground-check monitoring conductor is required, select Type G-GC.

## Technical data
Type G Portable Mining Power Cable (ICEA/NEMA/MSHA) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-g-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 600–2,000 V (DC shuttle cars & AC mining power)
Key data | Configurations | 2C+G / 3C / 4C (Flat 2C+G · Round 3C+3G / 4C+4G)
Key data | Conductor sizes | 8 AWG–500 kcmil (Flat 8–4/0 AWG · Round to 500 kcmil)
Key data | Max. conductor T | +90 °C (Dry & wet · 130 °C overload)
Key data | Min. operating T | −40 °C (Cold-bend & impact rated CPE/EPR)
Key data | Min. bend radius | 6 × D (6 × minor H (flat) or 6–8 × OD)
Electrical | Rated voltage | 600 to 2,000 V (Flat 2C+G); 2,000 V (Round 3C+3G & 4C+4G)
Electrical | Ampacity range (40 °C ambient) | 72 to 328 A (Flat 2C, 8 AWG–4/0 AWG); 59 to 487 A (Round 3C, 8 AWG–500 kcmil)
Electrical | Grounding conductors | Flat 2C: central tinned copper ground between power cores · Round 3C/4C: 3 or 4 interstitial tinned copper grounds (≥ 50 % of one phase core area)
Electrical | Ground-check conductor | None (specify Type G-GC when a yellow ground-check monitoring pilot is required)
Thermal | Max. continuous conductor temp. | +90 °C (dry or wet locations)
Thermal | Emergency overload / short-circuit | +130 °C emergency overload · +250 °C short-circuit
Thermal | Min. operating temperature | −40 °C (cold-bend and impact resistant)
Mechanical | Min. bending radius | 6 × minor thickness H (Flat 2C); 6 × OD up to 2.0 in OD and 8 × OD over 2.0 in OD (Round 3C/4C)
Mechanical | Conductor stranding | Flexible rope-lay stranded annealed tinned copper (133 to 532 strands in Flat 2C; up to 1,221 strands in 500 kcmil Round)
Mechanical | Outer jacket & reinforcement | Two-layer reinforced extra-heavy-duty thermoset jacket
Resistance | Flame resistance | MSHA 30 CFR Part 7 Subpart K flame test; CAN/CSA-C22.2 No. 96 FT4
Resistance | Abrasion, oil & environment | Oil, abrasion, cut, impact, ozone, water and sunlight resistant
Standards | Primary construction standard | ICEA S-75-381 / NEMA WC 58; CAN/CSA-C22.2 No. 96
Standards | Conductor standards | ASTM B172; ASTM B33
Identification | Power & ground identification | Flat 2C: Black, White + uninsulated/green ground · Round 3C: Black, White, Red + 3 grounds · Round 4C: Black, White, Red, Orange + 4 grounds
Identification | Outer jacket compound & colour | Black heavy-duty thermoset CPE
Identification | Surface legend & MSHA marking | Permanent indent/embossed or print legend with size, Type G, voltage, 90C and MSHA number

## Construction
Type G Portable Mining Power Cable (ICEA/NEMA/MSHA) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-g-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Power conductors | Flexible rope-lay stranded annealed tinned copper (2, 3 or 4 cores) | ASTM B172 / ASTM B33
2 | Primary insulation | 90 °C heat-, moisture- and ozone-resistant EPR (ethylene-propylene rubber) | ICEA S-75-381 Part 3
3 | Grounding conductor(s) | Flexible tinned copper ground between power cores (Flat 2C) or 3 / 4 interstitial grounds (Round 3C / 4C) | ICEA S-75-381 Table 3-3
4 | Reinforcing fibre | Synthetic yarn reinforcement between inner and outer jacket layers
5 | Outer jacket | Extra-heavy-duty thermoset chlorinated polyethylene (CPE), black (CSP, PCP, NBR or PVC optional) | ICEA S-75-381 Part 4 / MSHA
| Type G Flat 2C · 600–2,000 V | 8 AWG to 4/0 AWG — two parallel power cores (Black, White) with central grounding conductor
| Type G Round 3C · 2,000 V | 8 AWG to 500 kcmil — three power cores (Black, White, Red) with three symmetric interstitial grounds
| Type G Round 4C · 2,000 V | 8 AWG to 500 kcmil — four power cores (Black, White, Red, Orange) with four symmetric interstitial grounds

## Quality and supply
Type G Portable Mining Power Cable (ICEA/NEMA/MSHA) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-g-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | In-line high-voltage spark test — 100 % of insulated power conductors spark-tested prior to core lay-up | Every core
Routine test | Conductor DC resistance & AC high-voltage proof test — Verified on all power and grounding conductors per ICEA S-75-381 | Every drum
Sample test | Vertical flame chamber test — Self-extinguishing per MSHA 30 CFR Part 7 and CAN/CSA-C22.2 No. 96 | Production batch
Sample test | Laser profile & jacket wall verification — Dual-axis verification of minor/major dimensions and minimum jacket thickness | Every drum
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · TYPE G FLAT · 600–2000V · 90C · 2/C [size] + G · EPR/CPE · ICEA S-75-381 · P-MSHA
Supply | Delivery form: Heat-treated seaworthy wooden drums with solid wood battens and waterproof end caps
Supply | Lengths: Custom cut-to-length reels per shuttle-car or machine cable schedule
Supply | Optional jackets: Standard extra-heavy-duty black CPE; CSP, PCP, NBR or PVC compounds available on request
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | MOQ: None
Supply | Lead time: None