## Request a quote
Request a quotation for Type MP-GC
Application engineer · MV mine feeder cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-mp-gc-mine-power-feeder-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Type MP-GC Mine Power Feeder Cable (2–15 kV) – Sizes & dimensions · 5 kV baseline (11)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-mp-gc-mine-power-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 Part 5. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Power cores 3 × AWG/kcmil | Phase strands | Grounds (2) AWG/kcmil | Pilot (GC) AWG | Insulation in | Insulation mm | Jacket in | Jacket mm | Nominal OD in | Nominal OD mm | Weight ≈ lb/kft | Mass ≈ kg/km | Ampacity A (40 °C)
| Type MP-GC 5 kV · 3 × 6 AWG | 7 | 2 × 10 | 8 | 0.09 | 2.3 | 0.11 | 2.8 | 1.3 | 33 | 1060 | 1577 | 93
| Type MP-GC 5 kV · 3 × 4 AWG | 7 | 2 × 8 | 8 | 0.09 | 2.3 | 0.11 | 2.8 | 1.41 | 35.8 | 1441 | 2144 | 122
| Type MP-GC 5 kV · 3 × 2 AWG | 7 | 2 × 6 | 8 | 0.09 | 2.3 | 0.11 | 2.8 | 1.47 | 37.3 | 1827 | 2718 | 159
| Type MP-GC 5 kV · 3 × 1 AWG | 19 | 2 × 5 | 8 | 0.09 | 2.3 | 0.11 | 2.8 | 1.54 | 39.1 | 2168 | 3226 | 184
| Type MP-GC 5 kV · 3 × 1/0 AWG | 19 | 2 × 4 | 8 | 0.09 | 2.3 | 0.11 | 2.8 | 1.63 | 41.4 | 2602 | 3871 | 211
| Type MP-GC 5 kV · 3 × 2/0 AWG | 19 | 2 × 3 | 8 | 0.09 | 2.3 | 0.11 | 2.8 | 1.72 | 43.7 | 3010 | 4478 | 243
| Type MP-GC 5 kV · 3 × 3/0 AWG | 19 | 2 × 2 | 8 | 0.09 | 2.3 | 0.14 | 3.6 | 1.89 | 48 | 3265 | 4859 | 279
| Type MP-GC 5 kV · 3 × 4/0 AWG | 19 | 2 × 1 | 8 | 0.09 | 2.3 | 0.14 | 3.6 | 2.01 | 51 | 4190 | 6234 | 321
| Type MP-GC 5 kV · 3 × 250 kcmil | 37 | 2 × 1/0 | 8 | 0.09 | 2.3 | 0.14 | 3.6 | 2.1 | 53.3 | 4825 | 7179 | 355
| Type MP-GC 5 kV · 3 × 350 kcmil | 37 | 2 × 2/0 | 8 | 0.09 | 2.3 | 0.14 | 3.6 | 2.31 | 58.7 | 6062 | 9019 | 435
| Type MP-GC 5 kV · 3 × 500 kcmil | 37 | 2 × 4/0 | 8 | 0.09 | 2.3 | 0.14 | 3.6 | 2.59 | 65.8 | 8427 | 12538 | 536
Published table dimensions reflect 0.090 in (2.3 mm) nominal insulation thickness (ICEA S-75-381 5 kV 100 % insulation level, also used for 2/5 kV dual-rated feeders).
For 8 kV (100 % level = 0.115 in / 2.9 mm insulation) and 15 kV (100 % level = 0.175 in / 4.4 mm insulation), request project-specific dimensional drawings.

## Technical data
Type MP-GC Mine Power Feeder Cable (2–15 kV) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-mp-gc-mine-power-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 Part 5. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 2 to 15 kV (2, 5, 8 & 15 kV feeder classes)
Key data | Core arrangement | 3P + 2G + 1GC (3 shielded + 2 ground + 1 GC)
Key data | Size range | 6 AWG–500 kcmil (Class B (7, 19 or 37 strands))
Key data | Max. conductor T | +90 °C (EPR or XLPE · 130 °C overload)
Key data | Min. operating T | −40 °C (EPR/CPE (−25 °C XLPE/PVC))
Key data | Min. bend radius | 12 × OD (Fixed feeder installation)
Electrical | Rated voltage classes | 2 kV, 5 kV, 8 kV & 15 kV (100 % insulation level)
Electrical | Ampacity range | 93 to 536 A (90 °C conductor, 40 °C ambient in free air)
Electrical | Phase shielding | Extruded semiconductive conductor & insulation screens + helically applied copper tape shield
Electrical | Grounding conductors | Two uninsulated concentric-lay bare or tinned copper grounds (10 AWG to 4/0 AWG) in two outer interstices
Electrical | Ground-check pilot | One yellow EPR/PP or XLPE/PVC insulated copper conductor (8 AWG) in third interstice
Thermal | Max. continuous conductor temp. | +90 °C (EPR or XLPE, dry / wet)
Thermal | Min. operating temperature | −40 °C (EPR/CPE construction); −25 °C (XLPE/PVC construction)
Thermal | Emergency overload temperature | +130 °C
Thermal | Short-circuit temperature | +250 °C
Mechanical | Min. installation bend radius | 12 × OD (fixed / stationary feeder installation)
Mechanical | Phase conductor stranding | Compact or concentric-lay stranded annealed bare/tinned copper, Class B (7, 19 or 37 strands)
Mechanical | Installation duty | Stationary feeder distribution (aerial messenger, borehole, shaft, duct, tray or direct burial) — not for reeling/dragging
Resistance | Flame retardance | MSHA 30 CFR Part 7 flame test; UL 1072 / CSA C22.2 No. 96 FT4
Resistance | Chemical, oil & moisture | 90 °C wet/dry rated; heavy-duty CPE or PVC jacket resists mine water, oil, acids and alkalis
Resistance | Sunlight & weather | UV-stabilised black CPE or PVC outer jacket for exposed surface tray and aerial runs
Standards | Construction standard | ICEA S-75-381 / NEMA WC 58 Part 5; ICEA S-93-639 / NEMA WC 74
Standards | Conductor standard | ASTM B3 / ASTM B8 (Class B concentric or compact copper)
Standards | Safety & flame | MSHA 30 CFR Part 7; UL 1072 (MV-90); CSA C22.2 No. 96
Identification | Phase identification | Colour-coded phase tape under metallic shield (Black, White, Red) or numbered
Identification | Ground & ground-check | Grounds: 2 × bare copper · Ground-check: 1 × Yellow insulated 8 AWG
Identification | Insulation / jacket systems | EPR / Black CPE (2–15 kV) or XLPE / Black PVC (5–15 kV)

## Construction
Type MP-GC Mine Power Feeder Cable (2–15 kV) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-mp-gc-mine-power-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 Part 5. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase conductors (3) | Annealed bare or tinned copper, Class B compact/concentric stranding (7, 19 or 37 wires) | ASTM B3 / ASTM B8
2 | Conductor screen | Extruded thermoset semiconductive layer over phase conductor | ICEA S-75-381 Part 5
3 | Phase insulation | 90 °C EPR (ethylene propylene rubber) or tree-retardant XLPE
4 | Insulation screen | Extruded strip-type thermoset semiconductive insulation shield | ICEA S-75-381 Part 5
5 | Metallic phase shield | Helically applied annealed copper tape (overlapped) with phase identification tape | ICEA S-75-381 Part 5
6 | Grounding conductors (2) | Two uninsulated concentric-lay copper grounding conductors (10 AWG to 4/0 AWG) in two interstices contacting the copper shields
7 | Ground-check pilot (1) | One yellow EPR or XLPE insulated copper conductor (8 AWG) in third interstice
8 | Assembly binder tape | Reinforcing binder tape over cabled core assembly and polypropylene fillers
9 | Outer jacket | Heavy-duty flame-retardant black thermoset CPE (with EPR) or black PVC (with XLPE) | ICEA S-75-381 / MSHA / FT4
| EPR / CPE · 2–15 kV | Thermoset EPR insulation with heavy-duty black CPE jacket (−40 to +90 °C) for greater flexibility and cold impact
| XLPE / PVC · 5–15 kV | Cross-linked polyethylene (XLPE) insulation with flame-retardant black PVC jacket (−25 to +90 °C) for fixed tray/duct runs

## Quality and supply
Type MP-GC Mine Power Feeder Cable (2–15 kV) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-mp-gc-mine-power-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 Part 5. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | High-voltage AC withstand & partial discharge test — 100 % routine AC voltage and corona/PD test per ICEA S-75-381 Part 5 | Every shipping length
Routine test | Phase, ground & ground-check DC resistance — Verified on all 3 phase cores, 2 grounds and 8 AWG pilot | Every shipping length
Sample test | Vertical tray flame test — Self-extinguishing per MSHA 30 CFR Part 7 / UL 1072 / CSA FT4 | Production batch
Sample test | Dimensional & concentricity inspection — Insulation and jacket wall thickness verification | Every drum
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · TYPE MP-GC · 5000V · 90C · 3/C [size] · EPR/CPE · ICEA S-75-381 · FT4
Supply | Delivery form: Heavy-duty export fumigated wooden or steel drums sized to 12 × OD minimum bend radius
Supply | Lengths: Custom continuous feeder lengths for shafts, boreholes and main entries
Supply | Certificate: EN 10204 3.1 inspection certificate with HV & PD test results
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None