## Request a quote
Request a quotation for Type MV-105 Flexible Single-Conductor
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mv-105-flexible-single-conductor-medium-voltage-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Type MV-105 Flexible Single-Conductor – 15 kV (133 % Level) dimensions & NEC ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mv-105-flexible-single-conductor-medium-voltage-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1072 / ICEA S-93-639 (NEMA WC 74) / CSA C68.5. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Conductor size & Class I strands | Nominal Ø mm | Weight ≈ kg/km | Air 40°C A | Duct 20°C A | Series
| MV-105 Flex 2 AWG 15kV | 2 AWG (33.6 mm²) · 161×24 AWG | 24.9 | 820 | 215 | 165 | 15 kV (133 % Level · 5.59 mm EPR) Flexible Class I Tinned Cu
| MV-105 Flex 1/0 AWG 15kV | 1/0 AWG (53.5 mm²) · 259×24 AWG | 27.2 | 1060 | 290 | 215 | 15 kV (133 % Level · 5.59 mm EPR) Flexible Class I Tinned Cu
| MV-105 Flex 4/0 AWG 15kV | 4/0 AWG (107 mm²) · 532×24 AWG | 31.8 | 1680 | 445 | 320 | 15 kV (133 % Level · 5.59 mm EPR) Flexible Class I Tinned Cu
| MV-105 Flex 350 kcmil 15kV | 350 kcmil (177 mm²) · 882×24 AWG | 36.6 | 2490 | 615 | 430 | 15 kV (133 % Level · 5.59 mm EPR) Flexible Class I Tinned Cu
| MV-105 Flex 500 kcmil 15kV | 500 kcmil (253 mm²) · 1225×24 AWG | 40.6 | 3340 | 775 | 530 | 15 kV (133 % Level · 5.59 mm EPR) Flexible Class I Tinned Cu
| MV-105 Flex 750 kcmil 15kV | 750 kcmil (380 mm²) · 1850×24 AWG | 46.5 | 4780 | 1000 | 665 | 15 kV (133 % Level · 5.59 mm EPR) Flexible Class I Tinned Cu
Also available in 5 kV (90/115 mil EPR), 8 kV, 15 kV 100 % (175 mil EPR), 25 kV (260/320 mil EPR) and 35 kV (345/420 mil EPR).

## Technical data
Type MV-105 Flexible Single-Conductor – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mv-105-flexible-single-conductor-medium-voltage-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1072 / ICEA S-93-639 (NEMA WC 74) / CSA C68.5. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | UL 1072 / ICEA S (NEMA WC 74 & NEC Art. 328)
Key data | Voltage classes | 2.4 kV to 35 kV (5, 8, 15, 25 & 35 kV (100/133%))
Key data | Size range | 6 AWG to 1000 kc (Class I (24 AWG) / Class K (30 AWG))
Key data | Insulation | +105 °C EPR (+140 °C overload · +250 °C SC)
Key data | Shield system | Tinned Cu Braid/ (85%+ flexible braid or 5 mil tape)
Key data | Outer jacket | CPE or LSZH (CT) (Oil Res I/II, Sunlight & Burial)
Electrical | Voltage classes | 2.4 kV · 5 kV · 8 kV · 15 kV · 25 kV · 35 kV (100 % & 133 % levels)
Electrical | AC factory test voltage | 18 kV (5 kV) · 36 kV (15 kV) · 52 kV (25 kV) · 69 kV (35 kV) + PD ≤ 5 pC
Electrical | Max. DC resistance @ 20 °C | 0.348 Ω/km (1/0) · 0.138 Ω/km (4/0) · 0.058 Ω/km (500) · 0.039 Ω/km (750)
Electrical | Shield fault capacity | Tinned copper braid (~10–25 mm² eq.) carries ground fault & charging current
Thermal | Continuous conductor temp. | +105 °C Wet or Dry (UL 1072 Type MV-105)
Thermal | Emergency overload temp. | +140 °C (up to 100 hours/year)
Thermal | Short-circuit & cold bend | +250 °C short-circuit · -40 °C cold bend per UL 1072
Mechanical | 15 kV EPR wall thickness | 4.45 mm / 175 mil (100 % level) · 5.59 mm / 220 mil (133 % level)
Mechanical | Min. bend radius | 6 × OD to 8 × OD (braid-shielded flexible) · 12 × OD (tape-shielded)
Mechanical | Stranding flexibility | Class I (24 AWG / 0.51 mm) or Class K (30 AWG / 0.254 mm) rope lay
Resistance | Tray flame & fire rating | UL 1685 / IEEE 1202 / CSA FT4 vertical tray flame ('FOR CT USE')
Resistance | Oil, UV & Direct Burial | UL Oil Res I & II, 720-hour Sunlight Resistant & Direct Burial
Resistance | LSZH jacket option | Halogen-free low-smoke zero-halogen jacket available for tunnels/data halls
Standards | North American standards | UL 1072 · ICEA S-93-639 / NEMA WC 74 · CSA C68.5 · NEC Art. 328
Standards | Ampacity reference | NEC Table 310.60(C)(69) / (73) (+105 °C MV-105 tables)
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Surface print legend | TEBAOFLEX (UL) TYPE MV-105 15KV 133% EPR FLEXIBLE TINNED CU FOR CT USE SUN RES OIL RES I/II DIR BUR
Identification | Customs tariff (HS) | 8544.6010
Identification | Sequential footage marks | Printed every 1 ft (0.305 m) along outer jacket

## Construction
Type MV-105 Flexible Single-Conductor – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mv-105-flexible-single-conductor-medium-voltage-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1072 / ICEA S-93-639 (NEMA WC 74) / CSA C68.5. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class I (24 AWG) or Class K (30 AWG) rope-lay tinned copper | Extra-flexible rope-bunch stranded tin-coated annealed copper per ASTM B33 & ASTM B172 (6 AWG to 1000 kcmil)
2 | Triple-extruded semiconducting conductor & insulation screens | Separator tape + smooth thermoset semiconducting conductor screen and easy-peel outer semiconducting insulation screen
3 | +105 °C Discharge-Free EPR (Ethylene Propylene Rubber) dielectric | Lead-free, tree-retardant +105 °C EPR at 100 % or 133 % ICEA wall thickness (e.g., 175 mil / 4.45 mm on 15 kV 100 %; 220 mil / 5.59 mm on 15 kV 133 %)
4 | Flexible tinned copper braid shield (or 5 mil Cu tape + drain) | High-coverage (≥ 85 %) tinned copper wire braid shield (or 5 mil overlapped copper tape for static sweeps)
5 | Sunlight- & Oil-Resistant Black CPE (or Halogen-Free LSZH) jacket | Heavy-duty thermoset Chlorinated Polyethylene (CPE) or Low-Smoke Zero-Halogen polyolefin jacket (Black, or Red striped)
| Type MV-105 Flex 5 kV (100% / 133% · 90 / 115 mil EPR · 6 AWG–1000 kcmil) | 2.4 kV & 4.16 kV flexible motor lead, VFD and generator bus cable with Class I/K tinned Cu and tinned Cu braid shield
| Type MV-105 Flex 15 kV (100% 175 mil / 133% 220 mil EPR · 2 AWG–1000 kcmil) | 13.8 kV data-centre generator, substation switchgear and mobile transformer jumper cable
| Type MV-105 Flex 25 kV & 35 kV (260 / 345 mil EPR · 1/0 AWG–1000 kcmil) | 25 kV and 34.5 kV flexible collector, wind/BESS skid and mobile utility substation cable

## Quality and supply
Type MV-105 Flexible Single-Conductor – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mv-105-flexible-single-conductor-medium-voltage-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1072 / ICEA S-93-639 (NEMA WC 74) / CSA C68.5. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % ICEA S-93-639 AC dielectric withstand & partial discharge (< 5 pC) — Zero breakdown for 5 min (36 kV on 15 kV) and PD extinction at 1.5–2.0 × Uo | Every manufactured reel
Type test | UL 1685 / IEEE 1202 vertical tray flame, -40 °C cold bend & 720h UV test — Meets UL 1072 CT tray flame, cold impact and sunlight resistance | UL 1072 listing test
Sample test | Semiconducting insulation screen strip force (1.8 to 10.7 kgf / 4–24 lbf) — Clean, residue-free peel for cold-shrink / slip-on MV terminations | Per production batch
Standard / approval | UL 1072 Listed Type MV-105
Standard / approval | ICEA S-93-639 / NEMA WC 74
Standard / approval | IEEE 1202 / CSA FT4 Tray Rated
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (UL) TYPE MV-105 15KV 133% EPR FLEXIBLE TINNED CU FOR CT USE SUN RES OIL RES I/II DIR BUR
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP