## Request a quote
Request a quotation for Type MV-90 / MV-105 Distribution
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/mv-90-mv-105-medium-voltage-distribution-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Type MV-90 / MV-105 Distribution MV-90/MV-105 Medium-Voltage – 15 kV Cu & 35 kV Al feeder schedule (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/mv-90-mv-105-medium-voltage-distribution-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1072 / AEIC CS8 / ICEA S-93-639 / ICEA S-97-682. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Conductor, dielectric & shield | Nominal Ø mm | Weight ≈ kg/km | Tray/Air A | Duct 20°C A | Series
| MV-105 2 AWG Cu 15kV 133% | 2 AWG Cl.B Cu · 5.59mm EPR · CuTape | 23.6 | 760 | 215 | 165 | 15 kV (133% · 220 mil EPR) MV-105 Copper Tape Shield
| MV-105 2/0 AWG Cu 15kV 133% | 2/0 AWG Cl.B Cu · 5.59mm EPR · CuTape | 26.9 | 1180 | 330 | 245 | 15 kV (133% · 220 mil EPR) MV-105 Copper Tape Shield
| MV-105 4/0 AWG Cu 15kV 133% | 4/0 AWG Cl.B Cu · 5.59mm EPR · CuTape | 29.7 | 1610 | 445 | 320 | 15 kV (133% · 220 mil EPR) MV-105 Copper Tape Shield
| MV-105 500 kcmil Cu 15kV 133% | 500 kcmil Cl.B Cu · 5.59mm EPR · CuTape | 37.8 | 3210 | 775 | 530 | 15 kV (133% · 220 mil EPR) MV-105 Copper Tape Shield
| MV-90 1/0 AWG Al 35kV 100% | 1/0 AWG Al · 8.76mm TR-XLPE · WireSh | 33.5 | 920 | 200 | 155 | 35 kV (100% · 345 mil TR-XLPE) MV-90 Aluminum Collector
| MV-90 750 kcmil Al 35kV 100% | 750 kcmil Al · 8.76mm TR-XLPE · WireSh | 49.8 | 2640 | 685 | 475 | 35 kV (100% · 345 mil TR-XLPE) MV-90 Aluminum Collector
All sizes from 2 AWG to 1000 kcmil are available in both Copper and Aluminum across 5 kV, 8 kV, 15 kV, 25 kV and 35 kV.

## Technical data
Type MV-90 / MV-105 Distribution MV-90/MV-105 Medium-Voltage – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/mv-90-mv-105-medium-voltage-distribution-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1072 / AEIC CS8 / ICEA S-93-639 / ICEA S-97-682. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | UL 1072 / AEIC C (ICEA S-93-639 & S-97-682)
Key data | Voltage classes | 5 kV to 35 kV (5, 8, 15, 25 & 35 kV (100/133%))
Key data | Conductors | 2 AWG to 1000 kc (Class B Cu or 1350/AA-8000 Al)
Key data | Insulations | TR-XLPE or EPR (MV-90 (+90°C) · MV-105 (+105°C))
Key data | Metallic shield | Cu Tape or Wires (5 mil Cu tape or 1/3–Full wire)
Key data | Outer jacket | PVC / LLDPE / CP (Sunlight, CT Tray & Direct Burial)
Electrical | Voltage classes | 5 kV · 8 kV · 15 kV · 25 kV · 35 kV (100 % & 133 % insulation levels)
Electrical | AC factory test & PD | 18 kV (5 kV) · 36 kV (15 kV) · 52 kV (25 kV) · 69 kV (35 kV) + PD ≤ 5 pC
Electrical | Insulation levels (15 kV) | 100 % = 175 mil (4.45 mm) · 133 % = 220 mil (5.59 mm)
Electrical | Insulation levels (35 kV) | 100 % = 345 mil (8.76 mm) · 133 % = 420 mil (10.67 mm)
Thermal | Continuous conductor temp. | +90 °C (MV-90 TR-XLPE) · +105 °C (MV-105 EPR)
Thermal | Emergency overload temp. | +130 °C (MV-90) · +140 °C (MV-105)
Thermal | Short-circuit temperature | +250 °C
Mechanical | Min. bend radius | 12 × OD (copper tape shield) · 8 × OD (concentric wire shield)
Mechanical | Max. pulling tension | 0.008 lb/cmil (Cu) · 0.006 lb/cmil (Al) with pulling eye
Mechanical | Sidewall bearing pressure | Up to 1,000 lbs/ft (14.6 kN/m) around conduit sweeps
Resistance | Tray flame qualification | UL 1685 / IEEE 1202 / CSA FT4 vertical tray flame ('FOR CT USE' 1/0+)
Resistance | Sunlight & Direct Burial | 720-hour UV weatherometer & UL Direct Burial qualified
Resistance | Water-tree resistance | AEIC CS8 accelerated water-treeing test (AWTT) qualified
Standards | North American standards | UL 1072 · AEIC CS8 · ICEA S-93-639 (WC 74) · ICEA S-97-682 (WC 71)
Standards | NEC installation code | NFPA 70 (NEC) Article 328 & Table 310.60
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Surface print legend | TEBAOFLEX (UL) TYPE MV-105 (or MV-90) 15KV 133% EPR CU TAPE SHIELD FOR CT USE SUN RES DIR BUR AEIC CS8
Identification | Customs tariff (HS) | 8544.6010
Identification | Footage markings | Sequential 1-foot markings printed or indented on jacket

## Construction
Type MV-90 / MV-105 Distribution MV-90/MV-105 Medium-Voltage – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/mv-90-mv-105-medium-voltage-distribution-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1072 / AEIC CS8 / ICEA S-93-639 / ICEA S-97-682. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class B compressed annealed Copper or Aluminum conductor | Class B concentric compressed bare copper (ASTM B3 / B8) or 1350-H19 / AA-8000 aluminum (ASTM B231 / B800), optional longitudinal water-blocking compound (2 AWG to 1000 kcmil)
2 | True triple-extruded semiconducting conductor & insulation screens | Supersmooth thermoset semiconducting conductor screen co-extruded with dielectric and easy-strip outer semiconducting insulation screen
3 | TR-XLPE (+90 °C MV-90) or Discharge-Free EPR (+105 °C MV-105) | Tree-Retardant Cross-Linked Polyethylene (TR-XLPE) or +105 °C Ethylene Propylene Rubber (EPR) at 100 % or 133 % wall thickness
4 | 5 mil overlapped Copper Tape Shield or Concentric Wire Shield | 0.127 mm (5 mil) bare annealed copper tape applied helically with ≥ 12.5 %–25 % overlap (or concentric round copper wires for utility URD)
5 | Sunlight-Resistant PVC, LLDPE or CPE outer jacket | Black (with optional Red extruded stripes) flame-retardant PVC (CT tray rated), low-friction LLDPE (long underground pulls) or CPE jacket
| Type MV-105 Cu / EPR / CuTape / PVC (5 kV, 15 kV, 25 kV, 35 kV) | +105 °C Class B copper, EPR insulation, 5 mil copper tape shield and CT-rated PVC jacket for industrial trays and substations
| Type MV-90 / MV-105 Al / TR-XLPE or EPR / Wire Shield (15 kV & 35 kV) | 34.5 kV & 15 kV aluminum collector cable with concentric copper wire shield and LLDPE/PVC jacket for solar & wind farms

## Quality and supply
Type MV-90 / MV-105 Distribution MV-90/MV-105 Medium-Voltage – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/mv-90-mv-105-medium-voltage-distribution-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1072 / AEIC CS8 / ICEA S-93-639 / ICEA S-97-682. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % AEIC CS8 high-voltage AC withstand & partial discharge (< 5 pC) — Zero breakdown for 5 min and zero PD above 5 pC up to 2.0 × Uo | Every manufactured reel
Type test | AEIC CS8 cyclic aging, hot-creep & impulse breakdown qualification — Exceeds BIL lightning impulse and thermal load-cycle requirements | Type qualification
Sample test | Extruded insulation screen strip tension & semiconductor protrusion check — Clean 4–24 lbf strip tension and supersmooth interface per AEIC CS8 | Per production batch
Standard / approval | UL 1072 Listed MV-90 / MV-105
Standard / approval | AEIC CS8 Qualified
Standard / approval | ICEA S-93-639 & S-97-682
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (UL) TYPE MV-105 15KV 133% EPR 4/0 AWG CU FOR CT USE SUN RES DIR BUR AEIC CS8
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP