## Request a quote
Request a quotation for Type SHD-GC
Application engineer · MV & HV mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-shd-gc-cable-icea-nema-msha/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Type SHD-GC Shielded Mining Trailing Cable (2–25 kV) – Sizes & dimensions · 2–25 kV (45)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-shd-gc-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Voltage · size | Phase strands | Grounds / GC AWG/kcmil | Insulation in | Insulation mm | Jacket in | Jacket mm | Nominal OD in | Nominal OD mm | Weight ≈ lb/kft | Mass ≈ kg/km | Ampacity A (40 °C) | Series
| SHD-GC 2 kV · 3 × 6 AWG | 133 | 2×10 / 1×10 | 0.07 | 1.8 | 0.155 | 3.9 | 1.29 | 32.8 | 1069 | 1590 | 93 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 2 kV · 3 × 4 AWG | 259 | 2×8 / 1×10 | 0.07 | 1.8 | 0.155 | 3.9 | 1.4 | 35.6 | 1295 | 1927 | 122 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 2 kV · 3 × 2 AWG | 259 | 2×6 / 1×10 | 0.07 | 1.8 | 0.17 | 4.3 | 1.59 | 40.4 | 1778 | 2645 | 159 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 2 kV · 3 × 1 AWG | 259 | 2×5 / 1×8 | 0.08 | 2 | 0.19 | 4.8 | 1.76 | 44.7 | 2163 | 3218 | 184 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 2 kV · 3 × 1/0 AWG | 266 | 2×4 / 1×8 | 0.08 | 2 | 0.19 | 4.8 | 1.86 | 47.2 | 2508 | 3731 | 211 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 2 kV · 3 × 2/0 AWG | 323 | 2×3 / 1×8 | 0.08 | 2 | 0.205 | 5.2 | 2 | 50.8 | 3001 | 4465 | 243 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 2 kV · 3 × 3/0 AWG | 418 | 2×2 / 1×8 | 0.08 | 2 | 0.205 | 5.2 | 2.13 | 54.1 | 3470 | 5163 | 279 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 2 kV · 3 × 4/0 AWG | 532 | 2×1 / 1×8 | 0.08 | 2 | 0.22 | 5.6 | 2.31 | 58.7 | 4192 | 6237 | 321 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 2 kV · 3 × 250 kcmil | 627 | 2×1/0 / 1×6 | 0.095 | 2.4 | 0.22 | 5.6 | 2.51 | 63.8 | 5213 | 7756 | 355 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 2 kV · 3 × 350 kcmil | 888 | 2×2/0 / 1×6 | 0.095 | 2.4 | 0.235 | 6 | 2.81 | 71.4 | 6824 | 10153 | 435 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 2 kV · 3 × 500 kcmil | 1221 | 2×4/0 / 1×6 | 0.095 | 2.4 | 0.265 | 6.7 | 3.19 | 81 | 9014 | 13411 | 536 | SHD-GC 2 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 6 AWG | 133 | 2×10 / 1×8 | 0.11 | 2.8 | 0.185 | 4.7 | 1.56 | 39.6 | 1560 | 2322 | 93 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 4 AWG | 259 | 2×8 / 1×8 | 0.11 | 2.8 | 0.185 | 4.7 | 1.68 | 42.7 | 1895 | 2820 | 122 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 2 AWG | 259 | 2×6 / 1×8 | 0.11 | 2.8 | 0.205 | 5.2 | 1.87 | 47.5 | 2445 | 3639 | 159 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 1 AWG | 259 | 2×5 / 1×8 | 0.11 | 2.8 | 0.205 | 5.2 | 1.95 | 49.5 | 2800 | 4167 | 184 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 1/0 AWG | 266 | 2×4 / 1×8 | 0.11 | 2.8 | 0.22 | 5.6 | 2.08 | 52.8 | 3230 | 4807 | 211 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 2/0 AWG | 329 | 2×3 / 1×8 | 0.11 | 2.8 | 0.22 | 5.6 | 2.2 | 55.9 | 3800 | 5655 | 243 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 3/0 AWG | 418 | 2×2 / 1×8 | 0.11 | 2.8 | 0.235 | 6 | 2.36 | 59.9 | 4475 | 6660 | 279 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 4/0 AWG | 532 | 2×1 / 1×8 | 0.11 | 2.8 | 0.235 | 6 | 2.5 | 63.5 | 5265 | 7835 | 321 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 250 kcmil | 627 | 2×1/0 / 1×6 | 0.12 | 3 | 0.25 | 6.4 | 2.69 | 68.3 | 6105 | 9085 | 355 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 300 kcmil | 741 | 2×1/0 / 1×6 | 0.12 | 3 | 0.25 | 6.4 | 2.81 | 71.4 | 6875 | 10231 | 398 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 350 kcmil | 888 | 2×2/0 / 1×6 | 0.12 | 3 | 0.265 | 6.7 | 2.95 | 74.9 | 7795 | 11600 | 435 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 5 kV · 3 × 500 kcmil | 1221 | 2×4/0 / 1×6 | 0.12 | 3 | 0.28 | 7.1 | 3.31 | 84.1 | 10415 | 15499 | 536 | SHD-GC 5 kV · 6 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 4 AWG | 259 | 2×8 / 1×8 | 0.15 | 3.8 | 0.205 | 5.2 | 1.94 | 49.3 | 2308 | 3435 | 122 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 2 AWG | 259 | 2×6 / 1×8 | 0.15 | 3.8 | 0.22 | 5.6 | 2.12 | 53.8 | 2920 | 4345 | 159 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 1 AWG | 329 | 2×5 / 1×8 | 0.15 | 3.8 | 0.22 | 5.6 | 2.21 | 56.1 | 3292 | 4899 | 184 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 1/0 AWG | 259 | 2×4 / 1×8 | 0.15 | 3.8 | 0.22 | 5.6 | 2.32 | 58.9 | 3675 | 5469 | 211 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 2/0 AWG | 329 | 2×3 / 1×8 | 0.15 | 3.8 | 0.235 | 6 | 2.46 | 62.5 | 4304 | 6405 | 243 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 3/0 AWG | 413 | 2×2 / 1×8 | 0.15 | 3.8 | 0.25 | 6.4 | 2.62 | 66.5 | 5200 | 7738 | 279 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 4/0 AWG | 532 | 2×1 / 1×8 | 0.15 | 3.8 | 0.25 | 6.4 | 2.75 | 69.8 | 5840 | 8691 | 321 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 250 kcmil | 608 | 2×1/0 / 1×6 | 0.15 | 3.8 | 0.25 | 6.4 | 2.89 | 73.4 | 6774 | 10081 | 355 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 300 kcmil | 741 | 2×1/0 / 1×6 | 0.15 | 3.8 | 0.265 | 6.7 | 3.04 | 77.2 | 7423 | 11047 | 398 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 350 kcmil | 888 | 2×2/0 / 1×6 | 0.15 | 3.8 | 0.28 | 7.1 | 3.21 | 81.3 | 8543 | 12713 | 435 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 8 kV · 3 × 500 kcmil | 1221 | 2×4/0 / 1×6 | 0.15 | 3.8 | 0.295 | 7.5 | 3.56 | 90.4 | 11260 | 16757 | 536 | SHD-GC 8 kV · 4 AWG–500 kcmil
| SHD-GC 15 kV · 3 × 2 AWG | 259 | 2×6 / 1×8 | 0.21 | 5.3 | 0.235 | 6 | 2.41 | 61.2 | 3145 | 4679 | 164 | SHD-GC 15 kV · 2 AWG–4/0 AWG
| SHD-GC 15 kV · 3 × 1 AWG | 259 | 2×5 / 1×8 | 0.21 | 5.3 | 0.235 | 6 | 2.52 | 64 | 3567 | 5307 | 187 | SHD-GC 15 kV · 2 AWG–4/0 AWG
| SHD-GC 15 kV · 3 × 1/0 AWG | 266 | 2×4 / 1×8 | 0.21 | 5.3 | 0.25 | 6.4 | 2.64 | 67 | 3976 | 5916 | 215 | SHD-GC 15 kV · 2 AWG–4/0 AWG
| SHD-GC 15 kV · 3 × 2/0 AWG | 323 | 2×3 / 1×8 | 0.21 | 5.3 | 0.25 | 6.4 | 2.73 | 69.3 | 4526 | 6734 | 246 | SHD-GC 15 kV · 2 AWG–4/0 AWG
| SHD-GC 15 kV · 3 × 3/0 AWG | 418 | 2×2 / 1×8 | 0.21 | 5.3 | 0.265 | 6.7 | 2.9 | 73.7 | 5231 | 7783 | 283 | SHD-GC 15 kV · 2 AWG–4/0 AWG
| SHD-GC 15 kV · 3 × 4/0 AWG | 532 | 2×1 / 1×8 | 0.21 | 5.3 | 0.265 | 6.7 | 3.05 | 77.5 | 6033 | 8976 | 325 | SHD-GC 15 kV · 2 AWG–4/0 AWG
| SHD-GC 25 kV · 3 × 1 AWG | 259 | 2×5 / 1×8 | 0.26 | 6.6 | 0.265 | 6.7 | 2.95 | 74.9 | 5290 | 7872 | 191 | SHD-GC 25 kV · 1 AWG–4/0 AWG
| SHD-GC 25 kV · 3 × 1/0 AWG | 259 | 2×4 / 1×8 | 0.26 | 6.6 | 0.265 | 6.7 | 3.05 | 77.5 | 5800 | 8631 | 218 | SHD-GC 25 kV · 1 AWG–4/0 AWG
| SHD-GC 25 kV · 3 × 2/0 AWG | 329 | 2×3 / 1×8 | 0.26 | 6.6 | 0.28 | 7.1 | 3.2 | 81.3 | 6515 | 9695 | 249 | SHD-GC 25 kV · 1 AWG–4/0 AWG
| SHD-GC 25 kV · 3 × 3/0 AWG | 413 | 2×2 / 1×8 | 0.26 | 6.6 | 0.28 | 7.1 | 3.33 | 84.6 | 7215 | 10737 | 286 | SHD-GC 25 kV · 1 AWG–4/0 AWG
| SHD-GC 25 kV · 3 × 4/0 AWG | 532 | 2×1 / 1×8 | 0.26 | 6.6 | 0.295 | 7.5 | 3.5 | 88.9 | 8250 | 12277 | 327 | SHD-GC 25 kV · 1 AWG–4/0 AWG
Ampacity based on 90 °C conductor temperature at 40 °C ambient in free air (single cable) per ICEA S-75-381.
Grounds / GC column lists 2 × uninsulated tinned copper grounding conductors and 1 × yellow insulated ground-check pilot conductor.

## Technical data
Type SHD-GC Shielded Mining Trailing Cable (2–25 kV) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-shd-gc-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 2 to 25 kV (2, 5, 8, 15 & 25 kV grades)
Key data | Core arrangement | 3P + 2G + 1GC (3 shielded + 2 ground + 1 GC)
Key data | Size range | 6 AWG–500 kcmil (45 sizes across 5 voltages)
Key data | Max. conductor T | +90 °C (Dry & wet · 130 °C overload)
Key data | Min. operating T | −40 °C (Arctic mining flexibility)
Key data | Min. bend radius | 8 × OD (2–5 kV; 12 × OD at 8–25 kV)
Electrical | Rated voltage classes | 2,000 V · 5,000 V · 8,000 V · 15,000 V · 25,000 V (100 % insulation level)
Electrical | Ampacity range | 93 to 536 A (90 °C conductor, 40 °C ambient in free air)
Electrical | Phase shielding | Semiconductive conductor & insulation screens + tinned copper / textile composite braid shield (≥ 60 % coverage)
Electrical | Grounding conductors | Two uninsulated rope-lay tinned copper grounds in two outer interstices (in direct contact with phase shields)
Electrical | Ground-check pilot | One yellow EPR/PP-insulated tinned copper pilot (10, 8 or 6 AWG) in third interstice
Thermal | Max. continuous conductor temp. | +90 °C (dry / wet)
Thermal | Min. operating temperature | −40 °C
Thermal | Emergency overload temperature | +130 °C
Thermal | Short-circuit temperature | +250 °C
Mechanical | Min. bending radius | 8 × OD (2–5 kV); 12 × OD (8–25 kV) per ICEA S-75-381
Mechanical | Phase conductor stranding | Rope-lay stranded annealed tinned copper (133 to 1,221 strands)
Mechanical | Jacket reinforcement | Two-layer extra-heavy-duty thermoset CPE jacket with open-weave reinforcing cord
Resistance | Flame retardance | MSHA 30 CFR Part 7 flame test; CSA C22.2 No. 96 FT1 / FT4
Resistance | Abrasion, cut & crush | Extra-heavy-duty CPE sheath (3.9 to 7.5 mm radial wall) for open-pit haul roads and benches
Resistance | Oil, water & sunlight | 90 °C wet/dry rated; oil, chemical, ozone and UV sunlight resistant
Standards | Construction standard | ICEA S-75-381 / NEMA WC 58 (Tables 3-9 to 3-13)
Standards | Conductor standard | ASTM B172 / ASTM B33 (rope-lay tinned copper)
Standards | Mine safety & flame | MSHA 30 CFR Part 7; CSA C22.2 No. 96
Identification | Phase identification | Coloured tracer yarns in the metallic braid shield or phase tape (Black, White, Red)
Identification | Ground & ground-check | Grounds: 2 × uninsulated tinned copper · Ground-check: 1 × Yellow EPR/PP
Identification | Outer jacket | Black extra-heavy-duty thermoset CPE (high-visibility yellow/orange or TPU on request)

## Construction
Type SHD-GC Shielded Mining Trailing Cable (2–25 kV) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-shd-gc-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase conductors (3) | Rope-lay stranded annealed tinned copper (133 to 1,221 strands) | ASTM B172 / ASTM B33
2 | Conductor shield | Extruded semiconductive elastomer and/or semiconductive tape over phase conductor | ICEA S-75-381 stress control
3 | Phase insulation | 90 °C EPR (ethylene propylene rubber), 0.070 to 0.260 in (1.8 to 6.6 mm) by voltage class | ICEA S-75-381 Part 3
4 | Insulation shield | Extruded or taped semiconductive layer over phase insulation
5 | Metallic phase shield | Tinned copper wire and nylon/polyester composite braid (≥ 60 % coverage) with phase colour tracers | ICEA S-75-381 Part 3
6 | Grounding conductors (2) | Two uninsulated rope-lay tinned copper grounds in two outer interstices contacting the phase shields | 10 AWG to 4/0 AWG each
7 | Ground-check pilot (1) | One yellow EPR/PP-insulated tinned copper ground-check conductor (10, 8 or 6 AWG) in third interstice
8 | Reinforcing binder | Open-weave synthetic reinforcing cord embedded between inner and outer jacket layers
9 | Outer jacket | Two-layer extra-heavy-duty thermoset CPE (chlorinated polyethylene), 3.9 to 7.5 mm wall | ICEA S-75-381 / MSHA
| 2 kV & 5 kV classes | 6 AWG to 500 kcmil — 1.8–3.0 mm EPR wall, for continuous miners, loaders, drills and 4.16 kV shovels
| 8 kV, 15 kV & 25 kV classes | 4 AWG to 500 kcmil (8 kV) and 2/1 AWG to 4/0 AWG (15/25 kV) — 3.8–6.6 mm EPR wall for MV pit shovels & draglines

## Quality and supply
Type SHD-GC Shielded Mining Trailing Cable (2–25 kV) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-shd-gc-cable-icea-nema-msha/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | High-voltage AC & partial discharge test — 100 % routine AC withstand and corona/PD extinction per ICEA S-75-381 | Every shipping length
Routine test | Phase, ground & pilot DC resistance + shield continuity — Verified on all 3 phase cores, 3 metallic shields, 2 grounds and 1 GC pilot | Every shipping length
Sample test | Vertical flame resistance test — Self-extinguishing per MSHA 30 CFR Part 7 / CSA FT1 & FT4 | Production batch
Sample test | Laser diameter & sheath thickness inspection — Minimum jacket wall and nominal OD verification | Every drum
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · TYPE SHD-GC · [2000V–25000V] · 90C · 3/C [size] · EPR/CPE · ICEA S-75-381
Supply | Delivery form: Heavy-duty export fumigated wooden or steel reels sized to MV bending radius
Supply | Lengths: Custom continuous pit lengths per shovel, dragline or drill circuit
Supply | Certificate: EN 10204 3.1 inspection certificate with HV & PD test report per reel
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None