## Request a quote
Request a quotation for Type SH
Application engineer · mining & trailing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-sh-5-35kv-icea-msha-single-conductor-shielded-mv-portable-power-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
Type SH 5–35 kV MSHA Single-Conductor Shielded Power Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-sh-5-35kv-icea-msha-single-conductor-shielded-mv-portable-power-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 / MSHA. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| Type SH 15 kV 1/C 2/0 AWG (100% EPR) | 1 × 2/0 AWG (15 kV Shielded) | 329-wire Class K SnCu | 31.8 | 1490 | 13.4 | 255 | Type SH Construction Schedule (-40 to +90 °C)
| Type SH 15 kV 1/C 4/0 AWG (100% EPR) | 1 × 4/0 AWG (15 kV Shielded) | 532-wire Class K SnCu | 35.1 | 1980 | 21.3 | 280 | Type SH Construction Schedule (-40 to +90 °C)
| Type SH 15 kV 1/C 350 kcmil (100% EPR) | 1 × 350 kcmil (15 kV Shielded) | 882-wire Class K SnCu | 40.4 | 2910 | 35.3 | 325 | Type SH Construction Schedule (-40 to +90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per ICEA S-75-381 / NEMA WC 58 / MSHA.

## Electrical, optical & thermal p
Type SH 5–35 kV MSHA Single-Conductor Shielded Power Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-sh-5-35kv-icea-msha-single-conductor-shielded-mv-portable-power-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 / MSHA. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
1 × 2/0 AWG (15 kV Shielded) | 0.272 | 15 kV (300 A single free air) | -40 to +90 °C
1 × 4/0 AWG (15 kV Shielded) | 0.172 | 15 kV (400 A single free air) | -40 to +90 °C
1 × 350 kcmil (15 kV Shielded) | 0.104 | 15 kV (550 A single free air) | -40 to +90 °C
Every production length undergoes routine conductor DC resistance, high-voltage Spark/AC dielectric or OTDR continuity and dimensional verification.

## Technical data
Type SH 5–35 kV MSHA Single-Conductor Shielded Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-sh-5-35kv-icea-msha-single-conductor-shielded-mv-portable-power-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 / MSHA. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 15 kV (5 kV / 8 kV / 15 kV / 25 kV / 35 kV)
Key data | Operating temp. | -40 to +90 °C (Continuous mining & industrial duty)
Key data | Min. bend radius | 8 × OD (Fixed installation / dynamic routing)
Key data | Core / conductor | 1/C 2 AWG–750MCM (ASTM B172 Class K rope-lay tinned Cu)
Key data | Outer protection | 2-Layer EHD CPE (Extra-heavy-duty black crosslinked CPE)
Key data | Standard | ICEA S-75-381 (ICEA S-75-381 / NEMA WC 58 / MSHA)
Electrical | Rated voltage / transmission duty | 15 kV (ICEA S-75-381 / NEMA WC 58 / MSHA)
Electrical | Core / conductor construction | Flexible Conductor (1/C 4/0 AWG) — Rope-lay stranded annealed tinned copper (ASTM B33 / B172 Class K)
Electrical | Primary dielectric / buffering | Conductor Stress Shield (ESS) — Semiconductive tape + extruded thermosetting semiconductive layer
Thermal | Continuous operating temperature | -40 to +90 °C (mining & industrial service)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per ICEA S-75-381 / NEMA WC 58 / MSHA
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Separator Tape & EHD CPE Jacket — Reinforcing separator tape + two-layer extra-heavy-duty black CPE jacket
Mechanical | Minimum bending radius | 8 × OD
Mechanical | Crush, impact & abrasion duty | Heavy-duty mining rock-cut, impact and tensile protection per ICEA S-75-381 / NEMA WC 58 / MSHA
Resistance | Flame retardancy & mine fire safety | Self-extinguishing / flame-retardant mining jacket per ICEA S-75-381 / NEMA WC 58 / MSHA
Resistance | Mine water, oil & chemical resistance | Resistant to acidic mine water, hydraulic oils and abrasion per ICEA S-75-381 / NEMA WC 58 / MSHA
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | ICEA S-75-381 / NEMA WC 58 / MSHA
Standards | Flame & environmental test standards | IEC 60332 / MSHA / EN 60794 / IEC 60228
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | Type SH
Identification | Sheath colour & metre marking | Continuous metre-marked black mining outer sheath
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
Type SH 5–35 kV MSHA Single-Conductor Shielded Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-sh-5-35kv-icea-msha-single-conductor-shielded-mv-portable-power-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 / MSHA. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible Conductor (1/C 4/0 AWG) | Rope-lay stranded annealed tinned copper (ASTM B33 / B172 Class K)
2 | Conductor Stress Shield (ESS) | Semiconductive tape + extruded thermosetting semiconductive layer
3 | MV Primary Insulation (90 °C EPR) | High-dielectric ethylene propylene rubber (5.33 mm wall @ 15 kV)
4 | Insulation Screen & Composite Braid | Strippable semicon layer + tinned copper & polyamide braid shield (≥60%)
5 | Separator Tape & EHD CPE Jacket | Reinforcing separator tape + two-layer extra-heavy-duty black CPE jacket
| Type SH — Standard Mining Execution | Built to ICEA S-75-381 / NEMA WC 58 / MSHA with flexible conductor (1/c 4/0 awg) and separator tape & ehd cpe jacket
| Type SH — Custom Drum Length & Gland Kit | Available in custom shaft/roadway drum lengths or pre-terminated assemblies
| Type SH — Routine & Flame Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & flame test report

## Quality and supply
Type SH 5–35 kV MSHA Single-Conductor Shielded Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-sh-5-35kv-icea-msha-single-conductor-shielded-mv-portable-power-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 / MSHA. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (ICEA S-75-381 / NEMA WC 58 / MSHA) — DC resistance at 20 °C / optical attenuation and outer diameter within ICEA S-75-381 / NEMA WC 58 / MSHA tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (ICEA S-75-381 / NEMA WC 58 / MSHA) — Zero dielectric breakdown and verified insulation resistance over full production length | Every manufactured drum length
Type test | Flame propagation, mechanical crush & thermal ageing qualification (ICEA S-75-381 / NEMA WC 58 / MSHA) — Verified flame retardancy, mechanical integrity and thermal endurance across -40 to +90 °C | Type qualification & periodic lot audit
Standard / approval | ICEA S-75-381 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX Type SH ICEA S-75-381 15 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel mine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shaft/reeling lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP