## Request a quote
Request a quotation for UG7OG7KNR / RG7OG7KNR
Application engineer · petrochemical & industrial cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ug7og7knr-rg7og7knr-hepr-insulated-screen-armoured-industrial-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
UG7OG7KNR / RG7OG7KNR HEPR-Insulated Screen-Armoured Industrial – Dimensions, weights & free-air ampacity (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ug7og7knr-rg7og7knr-hepr-insulated-screen-armoured-industrial-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / CEI UNEL 35375 / CEI 20-22 II / IEC 60502-1. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Phase / Screen | Voltage | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | In air 30 °C A | Min. bend R mm | Series
| RG7OG7KNR 3×2.5/2.5 mm² | 3×2.5 / 2.5 mm² | 0.6/1 kV | 14.8 | 96 | 310 | 32 | 148 | RG7OG7KNR — Class 5 Flexible Copper HEPR Screen-Armoured Neoprene Cables
| RG7OG7KNR 3×6/6 mm² | 3×6 / 6 mm² | 0.6/1 kV | 18.2 | 230 | 515 | 54 | 182 | RG7OG7KNR — Class 5 Flexible Copper HEPR Screen-Armoured Neoprene Cables
| RG7OG7KNR 3×16/10 mm² | 3×16 / 10 mm² | 0.6/1 kV | 23.8 | 557 | 980 | 98 | 238 | RG7OG7KNR — Class 5 Flexible Copper HEPR Screen-Armoured Neoprene Cables
| RG7OG7KNR 3×35/16 mm² | 3×35 / 16 mm² | 0.6/1 kV | 30.2 | 1162 | 1740 | 158 | 302 | RG7OG7KNR — Class 5 Flexible Copper HEPR Screen-Armoured Neoprene Cables
| RG7OG7KNR 3×70/35 mm² | 3×70 / 35 mm² | 0.6/1 kV | 38.6 | 2352 | 3190 | 240 | 386 | RG7OG7KNR — Class 5 Flexible Copper HEPR Screen-Armoured Neoprene Cables
| RG7OG7KNR 3×120/70 mm² | 3×120 / 70 mm² | 0.6/1 kV | 47.5 | 4128 | 5180 | 340 | 475 | RG7OG7KNR — Class 5 Flexible Copper HEPR Screen-Armoured Neoprene Cables
| UG7OG7KNR 4×10/10 mm² | 4×10 / 10 mm² | 0.6/1 kV | 22.4 | 480 | 890 | 72 | 224 | UG7OG7KNR — Class 2 Stranded Copper HEPR Screen-Armoured Neoprene Cables
| UG7OG7KNR 4×50/25 mm² | 4×50 / 25 mm² | 0.6/1 kV | 36.8 | 2160 | 3120 | 185 | 368 | UG7OG7KNR — Class 2 Stranded Copper HEPR Screen-Armoured Neoprene Cables
| UG7OG7KNR 4×95/50 mm² | 4×95 / 50 mm² | 0.6/1 kV | 46.2 | 4128 | 5420 | 280 | 462 | UG7OG7KNR — Class 2 Stranded Copper HEPR Screen-Armoured Neoprene Cables
Full range covers 1 to 24 cores from 1.5 mm² to 240 mm² in both UG7OG7KNR and RG7OG7KNR.

## Technical data
UG7OG7KNR / RG7OG7KNR HEPR-Insulated Screen-Armoured Industrial – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ug7og7knr-rg7og7knr-hepr-insulated-screen-armoured-industrial-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / CEI UNEL 35375 / CEI 20-22 II / IEC 60502-1. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Italian std. | CEI 20-13 (CEI UNEL 35375 · IEC 60502-1)
Key data | Rated voltage | 0.6/1 kV (Umax = 1.2 kV AC / 1.5 kV DC)
Key data | Conductor | U (Cl.2) / R (U = rigid Class 2 · R = flex Cl.5)
Key data | Insulation (G7) | HEPR (+90 °C) (high-modulus EPR · +250 °C SC)
Key data | Screen-armour | Concentric Cu (copper wires/braid over inner G7)
Key data | Outer sheath | Neoprene (NR) (polychloroprene · CEI 20-22 II)
Electrical | Rated voltage (U₀/U) | 0.6/1 kV AC (Umax = 1.2 kV AC / 1.5 kV DC)
Electrical | Routine AC dielectric test voltage | 3.5 kV AC rms for 5 minutes + IR ≥ 500 MΩ·km
Electrical | Max. conductor DC resistance @ 20 °C | Per CEI EN 60228 Class 2 (U) or Class 5 (R)
Thermal | Operating temperature range | −25 °C (−35 °C fixed) to +90 °C conductor · +250 °C short-circuit (5 s)
Thermal | Thermal cycling & overload stability | Verified thermal ageing and short-circuit withstand per standard
Mechanical | Minimum bending radius | 10 × OD (RG7OG7KNR Class 5) · 12 × OD (UG7OG7KNR Class 2)
Mechanical | Installation & mechanical integrity | Engineered for industrial pulling, routing and support cleat loads
Resistance | Bunched vertical flame retardance | CEI 20-22 II & IEC 60332-3-22 Cat A non-fire-propagating
Resistance | Oil, hydrocarbon & chemical resistance | Polychloroprene (NR) jacket resists mineral oils, diesel, acids & ozone
Standards | Governing Italian & IEC standards | CEI 20-13, CEI UNEL 35375, CEI 20-22 II & IEC 60502-1
Standards | Factory QA & material compliance | EN 10204 3.1 routine test certificate · RoHS 2 & REACH compliant
Identification | Italian code breakdown | U/R (Cl.2/5 Cu) + G7 (HEPR) + OG7 (inner sheath) + K (Cu screen) + NR
Identification | Customs tariff (HS) | 8544.49

## Construction
UG7OG7KNR / RG7OG7KNR HEPR-Insulated Screen-Armoured Industrial – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ug7og7knr-rg7og7knr-hepr-insulated-screen-armoured-industrial-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / CEI UNEL 35375 / CEI 20-22 II / IEC 60502-1. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded (U = Class 2) or Flexible (R = Class 5) | CEI EN 60228 Class 2 ('U' in UG7OG7KNR) or Class 5 ('R' in RG7OG7KNR) annealed copper
2 | High-Modulus Ethylene Propylene Rubber (G7 / HEPR) | CEI 20-11 Type G7 cross-linked hard-grade HEPR (+90 °C continuous, +250 °C short-circuit)
3 | Extruded elastomeric inner sheath (OG7) | Vulcanised elastomeric inner covering over the laid-up cores
4 | Concentric copper wire / braid screen-armour (K) | Helical copper wires with counter-helix copper tape (or tinned-copper braid) over inner
5 | Polychloroprene / Neoprene outer sheath (NR) | Heavy-duty cross-linked Polychloroprene compound (CEI 20-22 II / IEC 60332-3-22 flame
| RG7OG7KNR (Class 5 Flexible Copper) | Flexible Class 5 ('R') conductor execution for vibrating motors, skids and tight refinery bends
| UG7OG7KNR (Class 2 Stranded Copper) | Rigid Class 2 ('U') conductor execution for long fixed pipe-rack and underground trench runs

## Quality and supply
UG7OG7KNR / RG7OG7KNR HEPR-Insulated Screen-Armoured Industrial – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ug7og7knr-rg7og7knr-hepr-insulated-screen-armoured-industrial-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / CEI UNEL 35375 / CEI 20-22 II / IEC 60502-1. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC 5-min dielectric withstand, screen continuity & conductor R_DC test — Zero breakdown; phase and concentric copper screen resistance verified | Every drum
Sample test | CEI 20-22 II vertical bunched flame & Neoprene (NR) hydrocarbon immersion test — Passes Category A bunched flame test and ASTM/IRM oil immersion | Periodic audit
Standard / approval | CEI 20-13 & CEI UNEL 35375 Compliant
Standard / approval | CEI 20-22 II / IEC 60332-3-22 Cat A Flame Retardant
Standard / approval | ATEX Zone 1 / Zone 2 (EN 60079-14) Suitable
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX UG7OG7KNR (or RG7OG7KNR) 0.6/1kV <size> CEI 20-13 CEI 20-22 II CE
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP