## Request a quote
Request a quotation for UL AWM 1007 / 1569
Application engineer · UL / CSA appliance & electronic wires
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ul-awm-1007-1569-hook-up-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
UL AWM 1007 / 1569 Hook-Up Wire – Dimensions & weights (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1007-1569-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1007 / 1569 · CSA C22.2 No. 210 TR-64. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² / AWG | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| UL 1007/1569 30 AWG (7/38) | 30 AWG (0.05 mm²) | 30 | 1 | 1.1 | 0 | 2 | 4 | 300 V PVC Hook-Up Wire (UL 1007 / 1569 · CSA TR-64, 30–16 AWG)
| UL 1007/1569 28 AWG (7/36) | 28 AWG (0.08 mm²) | 28 | 1.1 | 1.2 | 0 | 2 | 5 | 300 V PVC Hook-Up Wire (UL 1007 / 1569 · CSA TR-64, 30–16 AWG)
| UL 1007/1569 26 AWG (7/34) | 26 AWG (0.13 mm²) | 26 | 1.2 | 1.3 | 1 | 3 | 5 | 300 V PVC Hook-Up Wire (UL 1007 / 1569 · CSA TR-64, 30–16 AWG)
| UL 1007/1569 24 AWG (7/32) | 24 AWG (0.20 mm²) | 24 | 1.3 | 1.4 | 2 | 4 | 6 | 300 V PVC Hook-Up Wire (UL 1007 / 1569 · CSA TR-64, 30–16 AWG)
| UL 1007/1569 22 AWG (7/30) | 22 AWG (0.33 mm²) | 22 | 1.5 | 1.6 | 3 | 5 | 6 | 300 V PVC Hook-Up Wire (UL 1007 / 1569 · CSA TR-64, 30–16 AWG)
| UL 1007/1569 20 AWG (7/28) | 20 AWG (0.52 mm²) | 20 | 1.7 | 1.8 | 5 | 7 | 7 | 300 V PVC Hook-Up Wire (UL 1007 / 1569 · CSA TR-64, 30–16 AWG)
| UL 1007/1569 18 AWG (16/30) | 18 AWG (0.82 mm²) | 18 | 1.9 | 2 | 7 | 10 | 8 | 300 V PVC Hook-Up Wire (UL 1007 / 1569 · CSA TR-64, 30–16 AWG)
| UL 1007/1569 16 AWG (26/30) | 16 AWG (1.31 mm²) | 16 | 2.2 | 2.4 | 12 | 15 | 9 | 300 V PVC Hook-Up Wire (UL 1007 / 1569 · CSA TR-64, 30–16 AWG)
Dimensions and weights are typical values per UL 758 Style 1007 / 1569 · CSA C22.2 No. 210 TR-64. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
UL AWM 1007 / 1569 Hook-Up Wire – Electrical & current ratings (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1007-1569-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1007 / 1569 · CSA C22.2 No. 210 TR-64. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single wire in air 30 °C, A | Multi-core bundle 30 °C, A
0.05 | 30 | 395 | 1.0 | 0.8
0.08 | 28 | 248 | 1.5 | 1.2
0.13 | 26 | 155 | 2.5 | 2.0
0.2 | 24 | 95.5 | 3.5 | 2.8
0.33 | 22 | 57.8 | 6.0 | 4.5
0.52 | 20 | 34.6 | 10 | 7
0.82 | 18 | 24 | 14 | 11
1.31 | 16 | 15.1 | 20 | 15
Current ratings at 30 °C ambient in free air. Apply temperature and bundle grouping factors per applicable equipment standard.

## Technical data
UL AWM 1007 / 1569 Hook-Up Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1007-1569-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1007 / 1569 · CSA C22.2 No. 210 TR-64. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 300 V RMS (UL AWM 1007 / 1569 & CSA TR-64)
Key data | Temp. rating | 80 / 105 °C (UL 1007 (80 °C) · UL 1569 (105 °C))
Key data | Insulation wall | 0.41 mm (16 mil) (Nominal 1/64 inch extruded PVC wall)
Key data | Flame rating | UL VW-1 / FT1 (Vertical wire flame test compliant)
Key data | Bending radius | 4 × OD (4 × overall diameter fixed routing)
Key data | Size range | 30–16 AWG (0.05–1.31 mm² · stranded/solid CuSn)
Electrical | Rated voltage | 300 V RMS
Electrical | Dielectric withstand voltage | 1500 V AC for 1 min · 3000 V AC spark test
Electrical | Max. DC conductor resistance (20 °C) | 28 AWG: ≤ 216 Ω/km · 24 AWG: ≤ 84.2 Ω/km · 22 AWG: ≤ 53.2 Ω/km · 20 AWG: ≤ 33.2 Ω/km · 18 AWG: ≤ 21.0 Ω/km · 16 AWG: ≤ 13.2 Ω/km
Thermal | Temperature rating | −40 °C to +105 °C (UL 1569) / +80 °C (UL 1007) / +90 °C (CSA TR-64 / AWM I A/B)
Thermal | Short-circuit / solder heat | +150 °C to +250 °C (5 s)
Mechanical | Nominal insulation wall | 0.41 mm (0.016 in / 16 mil) minimum average, 0.33 mm (13 mil) minimum at any point
Mechanical | Min. bending radius | 4 × overall diameter (fixed chassis routing)
Mechanical | Automated processing | Concentric extrusion allows high-speed cut-and-strip without nicking tinned strands
Resistance | Flame retardance | UL 1581 VW-1 vertical wire flame test & CSA C22.2 FT1
Resistance | Oil, acid & solvent resistance | Passes UL 60 °C oil immersion, weak acid, alkali and fungus resistance requirements
Standards | UL AWM styles | UL 758 Style 1007 (80 °C, 300 V) & Style 1569 (105 °C, 300 V)
Standards | CSA certification | CSA C22.2 No. 210 Type TR-64 (90 °C) & CSA AWM I A/B (105 °C, 300 V, FT1)
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 phthalate-free compliant
Identification | Standard stock colours | Black, White, Red, Blue, Yellow, Green, Brown, Orange, Violet, Grey & Green-Yellow
Identification | Surface marking | E-File AWM STYLE 1007 80C / 1569 105C 300V VW-1 [AWG] CSA TR-64 90C FT1 TEBAOFLEX
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
UL AWM 1007 / 1569 Hook-Up Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1007-1569-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1007 / 1569 · CSA C22.2 No. 210 TR-64. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded or solid tinned copper | Stranded (7/38 to 26/30) or solid tinned annealed copper per ASTM B33 / B286 for rapid solderability and corrosion resistance | ASTM B33 · UL 758
2 | 0.41 mm (16 mil) 105 °C PVC dielectric | Extruded polyvinyl chloride compound meeting both UL Style 1007 (80 °C) and Style 1569 (105 °C) at 300 V RMS | UL 758 Style 1007 / 1569
3 | VW-1 / FT1 colour-coded PVC surface | Smooth, strip-clean outer PVC surface with sequential UL/CSA surface legend and 10 standard EIA colours | UL 1581 VW-1 · CSA FT1
| UL 1007 / 1569 · CSA TR-64 Stranded Tinned Copper (30–16 AWG) | Flexible 7-strand or 19/26-strand tinned copper for crimped harnesses and soldered PCB leads
| UL 1007 / 1569 · CSA TR-64 Solid Tinned Copper (26–18 AWG) | Formable solid tinned copper core for breadboards, push-in terminals and rigid point-to-point dressing

## Quality and supply
UL AWM 1007 / 1569 Hook-Up Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1007-1569-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1007 / 1569 · CSA C22.2 No. 210 TR-64. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage test — 1.5 kV AC (50/60 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / ASTM (tinned copper) | Every manufactured length
Sample test | Flame propagation test — IEC 60332-1-2 / UL VW-1 / ISO 6722-1 | Per production batch
Type test | Insulation & sheath material physical properties — UL 758 Style 1007 / 1569 · CSA C22.2 No. 210 TR-64 | Type approval
Standard / approval | UL 758 Style 1007 / 1569 · CSA C22.2 No. 210 TR-64
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | AWM STYLE 1007/1569 105C 300V VW-1 [AWG] CSA TR-64 FT1 TEBAOFLEX
Supply | Delivery form: Export wooden drums, reels or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums or spools with sealed ends
Supply | Conductor / colour options: Custom core counts, stripe combinations or cut harnesses on request