## Request a quote
Request a quotation for UL AWM 1015
Application engineer · UL 508A / NFPA 79 panel wires
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ul-awm-1015-equipment-and-machine-tool-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
UL AWM 1015 Equipment and Machine Tool Wire – Dimensions & weights (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1015-equipment-and-machine-tool-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1015 · UL 1063 MTW · CSA C22.2 No. 127 TEW. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² / AWG | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| UL 1015 26 AWG (7/34) | 26 AWG (0.13 mm²) | 26 | 1.9 | 2.1 | 1 | 6 | 8 | 600 V 105 °C Equipment & Machine Tool Wire (UL 1015 / MTW / CSA TEW, 26–10 AWG)
| UL 1015 24 AWG (7/32) | 24 AWG (0.20 mm²) | 24 | 2.1 | 2.2 | 2 | 7 | 9 | 600 V 105 °C Equipment & Machine Tool Wire (UL 1015 / MTW / CSA TEW, 26–10 AWG)
| UL 1015 22 AWG (7/30) | 22 AWG (0.33 mm²) | 22 | 2.2 | 2.4 | 3 | 9 | 10 | 600 V 105 °C Equipment & Machine Tool Wire (UL 1015 / MTW / CSA TEW, 26–10 AWG)
| UL 1015 20 AWG (10/30) | 20 AWG (0.52 mm²) | 20 | 2.4 | 2.6 | 5 | 11 | 10 | 600 V 105 °C Equipment & Machine Tool Wire (UL 1015 / MTW / CSA TEW, 26–10 AWG)
| UL 1015 / MTW 18 AWG (16/30) | 18 AWG (0.82 mm²) | 18 | 2.6 | 2.9 | 7 | 14 | 11 | 600 V 105 °C Equipment & Machine Tool Wire (UL 1015 / MTW / CSA TEW, 26–10 AWG)
| UL 1015 / MTW 16 AWG (26/30) | 16 AWG (1.31 mm²) | 16 | 2.9 | 3.1 | 12 | 20 | 13 | 600 V 105 °C Equipment & Machine Tool Wire (UL 1015 / MTW / CSA TEW, 26–10 AWG)
| UL 1015 / MTW 14 AWG (41/30) | 14 AWG (2.08 mm²) | 14 | 3.3 | 3.5 | 20 | 28 | 14 | 600 V 105 °C Equipment & Machine Tool Wire (UL 1015 / MTW / CSA TEW, 26–10 AWG)
| UL 1015 / MTW 12 AWG (65/30) | 12 AWG (3.31 mm²) | 12 | 3.7 | 4 | 31 | 42 | 16 | 600 V 105 °C Equipment & Machine Tool Wire (UL 1015 / MTW / CSA TEW, 26–10 AWG)
| UL 1015 / MTW 10 AWG (105/30) | 10 AWG (5.26 mm²) | 10 | 4.3 | 4.7 | 50 | 64 | 19 | 600 V 105 °C Equipment & Machine Tool Wire (UL 1015 / MTW / CSA TEW, 26–10 AWG)
Dimensions and weights are typical values per UL 758 Style 1015 · UL 1063 MTW · CSA C22.2 No. 127 TEW. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
UL AWM 1015 Equipment and Machine Tool Wire – Electrical & current ratings (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1015-equipment-and-machine-tool-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1015 · UL 1063 MTW · CSA C22.2 No. 127 TEW. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single wire in air 30 °C, A | Multi-core bundle 30 °C, A
0.13 | 26 | 155 | 2.5 | 2.0
0.2 | 24 | 95.5 | 3.5 | 2.8
0.33 | 22 | 57.8 | 6.0 | 4.5
0.52 | 20 | 34.6 | 10 | 7
0.82 | 18 | 24 | 14 | 11
1.31 | 16 | 15.1 | 20 | 15
2.08 | 14 | 9.8 | 27 | 21
3.31 | 12 | 6.2 | 36 | 27
5.26 | 10 | 3.88 | 50 | 36
Current ratings at 30 °C ambient in free air. Apply temperature and bundle grouping factors per applicable equipment standard.

## Technical data
UL AWM 1015 Equipment and Machine Tool Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1015-equipment-and-machine-tool-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1015 · UL 1063 MTW · CSA C22.2 No. 127 TEW. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 600 V RMS (UL 1015 / UL 1063 MTW / CSA TEW)
Key data | Temp. rating | 105 °C / MTW 90 (105 °C UL 1015 & TEW · 60 °C oil/wet)
Key data | Insulation wall | 0.79 mm (30 mil) (Nominal 2/64 inch extruded PVC wall)
Key data | Flame rating | UL VW-1 / FT1 (Vertical flame test compliant)
Key data | Bending radius | 4 × OD (4 × overall diameter fixed duct routing)
Key data | Size range | 26–10 AWG (0.13–5.26 mm² (larger in 1028/1283/1284))
Electrical | Rated voltage | 600 V RMS
Electrical | Dielectric withstand voltage | 2000 V AC for 1 min · 6000 V AC spark test
Electrical | Max. DC conductor resistance (20 °C) | 22 AWG: ≤ 53.2 Ω/km · 18 AWG: ≤ 21.0 Ω/km · 16 AWG: ≤ 13.2 Ω/km · 14 AWG: ≤ 8.28 Ω/km · 12 AWG: ≤ 5.21 Ω/km · 10 AWG: ≤ 3.28 Ω/km
Thermal | Temperature rating | −40 °C to +105 °C (UL 1015 & CSA TEW dry) · +90 °C dry / +60 °C wet & oil (UL 1063 MTW)
Thermal | Short-circuit / solder heat | +150 °C to +250 °C (5 s)
Mechanical | Nominal insulation wall | 0.79 mm (0.031 in / 30 mil) minimum average, 0.71 mm (28 mil) minimum at any point
Mechanical | Min. bending radius | 4 × overall diameter (fixed panel routing)
Resistance | Flame retardance | UL 1581 VW-1 & CSA FT1 vertical flame tests
Resistance | Oil & coolant resistance | UL 1063 MTW & CSA TEW 60 °C oil immersion and cutting-fluid splash resistant
Standards | UL standards | UL 758 AWM Style 1015 & UL 1063 Machine Tool Wire (MTW, 16–10 AWG)
Standards | CSA & NFPA compliance | CSA C22.2 No. 127 Equipment Wire Type TEW · NFPA 79 & UL 508A compliant
Standards | European harmonisation option | Available multi-norm H05V-K / H07V-K + UL 1015 / MTW / CSA TEW for global control cabinets
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | NFPA 79 panel colours | Black (AC/DC power), Red (AC control), Blue (DC control), White (neutral), Green-Yellow (PE), Orange (interlock)
Identification | Surface marking | E-File AWM STYLE 1015 105C 600V VW-1 — MTW 90C — CSA TEW 105C 600V FT1 [AWG] TEBAOFLEX
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
UL AWM 1015 Equipment and Machine Tool Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1015-equipment-and-machine-tool-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1015 · UL 1063 MTW · CSA C22.2 No. 127 TEW. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded tinned or bare copper | Flexible stranded tinned or bare annealed copper per ASTM B33 / B8 / UL 1063 (26 AWG to 10 AWG; companion Styles 1028/1283/1284 up to 4/0 AWG) | ASTM B33 · UL 758 · UL 1063
2 | 0.79 mm (30 mil) 105 °C PVC dielectric | Heavy-wall 2/64-inch polyvinyl chloride rated 600 V RMS at 105 °C dry and 60 °C in oil/water | UL 758 Style 1015 · UL 1063 MTW
3 | VW-1 / FT1 oil-resistant PVC finish | Smooth, abrasion-resistant outer surface facilitating pull-through in slotted panel trunking and conduit | UL 1581 VW-1 · CSA C22.2 No. 127 TEW
| UL 1015 / MTW / TEW Tinned Copper (26–10 AWG) | Corrosion-resistant tinned copper strands for humid environments, soldering and marine/industrial panels
| UL 1015 / MTW / TEW Bare Copper (18–10 AWG) | Fine-stranded bare copper for standard UL 508A / NFPA 79 ferrules and compression lugs
| Heavy Gauge Companion Styles 1028 / 1283 / 1284 (8 AWG–4/0 AWG) | 600 V 105 °C MTW / TEW power distribution panel leads with thicker insulation walls

## Quality and supply
UL AWM 1015 Equipment and Machine Tool Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1015-equipment-and-machine-tool-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1015 · UL 1063 MTW · CSA C22.2 No. 127 TEW. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage test — 2.0 kV AC (50/60 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / ASTM (tinned copper) | Every manufactured length
Sample test | Flame propagation test — IEC 60332-1-2 / UL VW-1 / ISO 6722-1 | Per production batch
Type test | Insulation & sheath material physical properties — UL 758 Style 1015 · UL 1063 MTW · CSA C22.2 No. 127 TEW | Type approval
Standard / approval | UL 758 Style 1015 · UL 1063 MTW · CSA C22.2 No. 127 TEW
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | AWM STYLE 1015 105C 600V VW-1 MTW CSA TEW FT1 [AWG] TEBAOFLEX
Supply | Delivery form: Export wooden drums, reels or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums or spools with sealed ends
Supply | Conductor / colour options: Custom core counts, stripe combinations or cut harnesses on request