## Request a quote
Request a quotation for UL AWM 1061
Application engineer · UL / CSA electronic hook-up wires
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ul-awm-1061-sr-pvc-hook-up-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
UL AWM 1061 SR-PVC Hook-Up Wire – Dimensions & weights (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1061-sr-pvc-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1061 · CSA C22.2 No. 210 AWM I A/B. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² / AWG | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| UL 1061 30 AWG (7/38) | 30 AWG (0.05 mm²) | 30 | 0.7 | 0.8 | 0 | 1 | 3 | 300 V Thin-Wall Semi-Rigid PVC Hook-Up Wire (UL 1061 · CSA AWM I A/B, 30–16 AWG)
| UL 1061 28 AWG (7/36) | 28 AWG (0.08 mm²) | 28 | 0.8 | 0.9 | 0 | 2 | 4 | 300 V Thin-Wall Semi-Rigid PVC Hook-Up Wire (UL 1061 · CSA AWM I A/B, 30–16 AWG)
| UL 1061 26 AWG (7/34) | 26 AWG (0.13 mm²) | 26 | 0.9 | 1 | 1 | 2 | 4 | 300 V Thin-Wall Semi-Rigid PVC Hook-Up Wire (UL 1061 · CSA AWM I A/B, 30–16 AWG)
| UL 1061 24 AWG (7/32) | 24 AWG (0.20 mm²) | 24 | 1 | 1.1 | 2 | 3 | 5 | 300 V Thin-Wall Semi-Rigid PVC Hook-Up Wire (UL 1061 · CSA AWM I A/B, 30–16 AWG)
| UL 1061 22 AWG (7/30) | 22 AWG (0.33 mm²) | 22 | 1.2 | 1.3 | 3 | 4 | 5 | 300 V Thin-Wall Semi-Rigid PVC Hook-Up Wire (UL 1061 · CSA AWM I A/B, 30–16 AWG)
| UL 1061 20 AWG (7/28) | 20 AWG (0.52 mm²) | 20 | 1.4 | 1.5 | 5 | 6 | 6 | 300 V Thin-Wall Semi-Rigid PVC Hook-Up Wire (UL 1061 · CSA AWM I A/B, 30–16 AWG)
| UL 1061 18 AWG (16/30) | 18 AWG (0.82 mm²) | 18 | 1.6 | 1.8 | 7 | 9 | 7 | 300 V Thin-Wall Semi-Rigid PVC Hook-Up Wire (UL 1061 · CSA AWM I A/B, 30–16 AWG)
| UL 1061 16 AWG (26/30) | 16 AWG (1.31 mm²) | 16 | 1.9 | 2 | 12 | 14 | 8 | 300 V Thin-Wall Semi-Rigid PVC Hook-Up Wire (UL 1061 · CSA AWM I A/B, 30–16 AWG)
Dimensions and weights are typical values per UL 758 Style 1061 · CSA C22.2 No. 210 AWM I A/B. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
UL AWM 1061 SR-PVC Hook-Up Wire – Electrical & current ratings (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1061-sr-pvc-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1061 · CSA C22.2 No. 210 AWM I A/B. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single wire in air 30 °C, A | Multi-core bundle 30 °C, A
0.05 | 30 | 395 | 1.0 | 0.8
0.08 | 28 | 248 | 1.5 | 1.2
0.13 | 26 | 155 | 2.5 | 2.0
0.2 | 24 | 95.5 | 3.5 | 2.8
0.33 | 22 | 57.8 | 6.0 | 4.5
0.52 | 20 | 34.6 | 10 | 7
0.82 | 18 | 24 | 14 | 11
1.31 | 16 | 15.1 | 20 | 15
Current ratings at 30 °C ambient in free air. Apply temperature and bundle grouping factors per applicable equipment standard.

## Technical data
UL AWM 1061 SR-PVC Hook-Up Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1061-sr-pvc-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1061 · CSA C22.2 No. 210 AWM I A/B. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 300 V RMS (UL AWM Style 1061 & CSA AWM I A/B)
Key data | Temp. rating | 80 °C (−20 °C to +80 °C continuous)
Key data | Insulation wall | 0.25 mm (10 mil) (Semi-rigid PVC (SR-PVC) thin wall)
Key data | Flame rating | UL VW-1 / FT1 (Vertical wire flame test compliant)
Key data | Cut-through resist | High (SR-PVC) (High-durometer semi-rigid vinyl compound)
Key data | Size range | 30–16 AWG (0.05–1.31 mm² · stranded/solid CuSn)
Electrical | Rated voltage | 300 V RMS
Electrical | Dielectric withstand voltage | 1500 V AC for 1 min · 3000 V AC spark test
Electrical | Max. DC conductor resistance (20 °C) | 28 AWG: ≤ 216 Ω/km · 26 AWG: ≤ 135 Ω/km · 24 AWG: ≤ 84.2 Ω/km · 22 AWG: ≤ 53.2 Ω/km · 20 AWG: ≤ 33.2 Ω/km · 18 AWG: ≤ 21.0 Ω/km
Thermal | Temperature rating | −20 °C to +80 °C continuous
Thermal | Short-circuit / solder heat | +150 °C to +250 °C (5 s)
Mechanical | Nominal insulation wall | 0.25 mm (0.010 in / 10 mil) minimum average, 0.20 mm (8 mil) minimum at any point
Mechanical | Min. bending radius | 4 × overall diameter
Mechanical | Space & weight reduction | Up to 25 % smaller diameter and 35 % less bundle area than UL 1007 (16-mil wall)
Resistance | Flame retardance | UL 1581 VW-1 vertical wire flame test & CSA C22.2 FT1
Resistance | Pinch & cut-through resistance | Semi-rigid PVC resists chassis burrs, cable ties and IDC contact blades
Standards | UL AWM style | UL 758 Appliance Wiring Material Style 1061 (300 V, 80 °C)
Standards | CSA certification | CSA C22.2 No. 210 AWM Class I Group A/B (80 °C, 300 V, FT1)
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Standard stock colours | Black, White, Red, Blue, Yellow, Green, Brown, Orange, Violet & Grey
Identification | Surface marking | AWM STYLE 1061 80C 300V VW-1 CSA I A/B 80C 300V FT1 TEBAOFLEX
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
UL AWM 1061 SR-PVC Hook-Up Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1061-sr-pvc-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1061 · CSA C22.2 No. 210 AWM I A/B. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded or solid tinned copper | Concentric or bunched 7-strand / 19-strand or solid tinned annealed copper (30 AWG to 16 AWG) per ASTM B33 | ASTM B33 · UL 758
2 | 0.25 mm (10 mil) semi-rigid PVC (SR-PVC) | High-durometer semi-rigid polyvinyl chloride compound providing mechanical pinch and edge cut-through protection at 0.25 mm wall | UL 758 Style 1061
3 | Slick low-friction VW-1 / FT1 finish | Hard, clean-stripping surface ideal for automatic cut-strip-terminate machines and insulation displacement connectors (IDC) | UL 1581 VW-1 · CSA FT1
| UL 1061 Stranded Tinned Copper (30–16 AWG) | 7-strand to 26-strand tinned copper for automated crimp-housing and multi-pin harness assembly
| UL 1061 Solid Tinned Copper (28–18 AWG) | Solid tinned copper conductor that holds its formed routing shape along chassis walls and backplanes

## Quality and supply
UL AWM 1061 SR-PVC Hook-Up Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-1061-sr-pvc-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 1061 · CSA C22.2 No. 210 AWM I A/B. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage test — 1.5 kV AC (50/60 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / ASTM (tinned copper) | Every manufactured length
Sample test | Flame propagation test — IEC 60332-1-2 / UL VW-1 / ISO 6722-1 | Per production batch
Type test | Insulation & sheath material physical properties — UL 758 Style 1061 · CSA C22.2 No. 210 AWM I A/B | Type approval
Standard / approval | UL 758 Style 1061 · CSA C22.2 No. 210 AWM I A/B
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | AWM STYLE 1061 80C 300V VW-1 CSA I A/B FT1 TEBAOFLEX
Supply | Delivery form: Export wooden drums, reels or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums or spools with sealed ends
Supply | Conductor / colour options: Custom core counts, stripe combinations or cut harnesses on request