## Request a quote
Request a quotation for UL AWM 3173 / SIS
Application engineer · utility switchgear & UL 44 SIS wires
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ul-awm-3173-sis-switchboard-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
UL AWM 3173 / SIS Switchboard Wire – Dimensions & weights (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3173-sis-switchboard-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 44 Type SIS · UL 758 Style 3173 · CSA CL1251. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² / AWG | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| UL 3173 20 AWG (10/30) | 20 AWG (0.52 mm²) | 20 | 2.3 | 2.5 | 5 | 10 | 10 | 600 V Switchboard & Relay Panel Wire (UL 44 SIS / AWM 3173, 20–10 AWG)
| UL 3173 / SIS 18 AWG | 18 AWG (0.82 mm²) | 18 | 2.6 | 2.8 | 7 | 13 | 11 | 600 V Switchboard & Relay Panel Wire (UL 44 SIS / AWM 3173, 20–10 AWG)
| UL 3173 / SIS 16 AWG | 16 AWG (1.31 mm²) | 16 | 2.9 | 3.1 | 12 | 19 | 12 | 600 V Switchboard & Relay Panel Wire (UL 44 SIS / AWM 3173, 20–10 AWG)
| UL 3173 / SIS 14 AWG | 14 AWG (2.08 mm²) | 14 | 3.2 | 3.5 | 20 | 27 | 14 | 600 V Switchboard & Relay Panel Wire (UL 44 SIS / AWM 3173, 20–10 AWG)
| UL 3173 / SIS 12 AWG | 12 AWG (3.31 mm²) | 12 | 3.7 | 4 | 31 | 40 | 16 | 600 V Switchboard & Relay Panel Wire (UL 44 SIS / AWM 3173, 20–10 AWG)
| UL 3173 / SIS 10 AWG | 10 AWG (5.26 mm²) | 10 | 4.3 | 4.7 | 50 | 61 | 19 | 600 V Switchboard & Relay Panel Wire (UL 44 SIS / AWM 3173, 20–10 AWG)
| UL 3173 / SIS 8 AWG | 8 AWG (8.37 mm²) | 8 | 5.9 | 6.4 | 80 | 104 | 26 | 600 V Heavy Switchgear & CT/Motor Leads (UL 44 SIS / AWM 3173, 8–2 AWG)
| UL 3173 / SIS 6 AWG | 6 AWG (13.3 mm²) | 6 | 7.5 | 8.1 | 127 | 165 | 32 | 600 V Heavy Switchgear & CT/Motor Leads (UL 44 SIS / AWM 3173, 8–2 AWG)
| UL 3173 / SIS 4 AWG | 4 AWG (21.2 mm²) | 4 | 8.7 | 9.5 | 203 | 252 | 38 | 600 V Heavy Switchgear & CT/Motor Leads (UL 44 SIS / AWM 3173, 8–2 AWG)
| UL 3173 / SIS 2 AWG | 2 AWG (33.6 mm²) | 2 | 10.2 | 11.1 | 322 | 385 | 44 | 600 V Heavy Switchgear & CT/Motor Leads (UL 44 SIS / AWM 3173, 8–2 AWG)
Dimensions and weights are typical values per UL 44 Type SIS · UL 758 Style 3173 · CSA CL1251. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
UL AWM 3173 / SIS Switchboard Wire – Electrical & current ratings (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3173-sis-switchboard-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 44 Type SIS · UL 758 Style 3173 · CSA CL1251. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single wire in air 30 °C, A | Multi-core bundle 30 °C, A
0.52 | 20 | 34.6 | 10 | 7
0.82 | 18 | 24 | 14 | 11
1.31 | 16 | 15.1 | 20 | 15
2.08 | 14 | 9.8 | 27 | 21
3.31 | 12 | 6.2 | 36 | 27
5.26 | 10 | 3.88 | 50 | 36
8.37 | 8 | 2.42 | 68 | 48
13.3 | 6 | 1.48 | 92 | 65
21.2 | 4 | 0.92 | 125 | 88
33.6 | 2 | 0.58 | 165 | 115
Current ratings at 30 °C ambient in free air. Apply temperature and bundle grouping factors per applicable equipment standard.

## Technical data
UL AWM 3173 / SIS Switchboard Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3173-sis-switchboard-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 44 Type SIS · UL 758 Style 3173 · CSA CL1251. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 600 V RMS (UL 44 Type SIS & UL AWM 3173 / CL1251)
Key data | Temp. rating | 90 °C / 125 °C (90 °C (UL 44 SIS) · 125 °C (UL 3173))
Key data | Insulation wall | 0.76 mm (30 mil) (30 mil (22–10 AWG) · 45–80 mil (8–4/0))
Key data | Flame rating | VW-1 / FT1 / FT2 (UL 44 vertical flame & VW-1 / CSA FT1)
Key data | Short-circuit | +250 °C (Thermoset XLPE resists CT/PT fault heat)
Key data | Size range | 22–4/0 AWG (0.33–107 mm² · Class B or flex CuSn)
Electrical | Rated voltage | 600 V RMS
Electrical | Dielectric withstand voltage | 2000 V AC for 1 min · 6000 V AC spark test
Electrical | Max. DC conductor resistance (20 °C) | 18 AWG: ≤ 21.0 Ω/km · 16 AWG: ≤ 13.2 Ω/km · 14 AWG: ≤ 8.28 Ω/km · 12 AWG: ≤ 5.21 Ω/km · 10 AWG: ≤ 3.28 Ω/km
Thermal | Continuous temperature rating | +90 °C dry (UL 44 Type SIS NEC rating) · +125 °C continuous (UL AWM Style 3173 & CSA CL1251)
Thermal | Overload & short-circuit rating | +130 °C emergency overload · +250 °C short-circuit rating
Mechanical | Nominal insulation wall | 22–10 AWG: 0.76 mm (30 mil) · 8 AWG: 1.14 mm (45 mil) · 6–2 AWG: 1.52 mm (60 mil)
Mechanical | Min. bending radius | 4 × overall diameter (fixed switchboard routing)
Resistance | Flame retardance | UL 44 Horizontal / Vertical flame test, UL 1581 VW-1 & CSA FT1 / FT2 (IEEE 383 / VW-1 utility grade)
Resistance | Crush, oil & varnish resistance | Thermoset XLPE resists terminal screw creep, oil mist, ozone and Class F varnish baking
Standards | Primary switchboard standard | UL 44 Type SIS (Switchboard Wire, 600 V, 90 °C) & NEC Article 310 / ANSI C37.20
Standards | Appliance & motor lead standards | UL 758 AWM Style 3173 (600 V, 125 °C) & CSA C22.2 No. 210 Type CL1251 (or CSA SIS)
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Utility switchboard colours | Grey (standard utility relay colour), Black, White, Red, Blue, Yellow, Green, Orange, Brown & Violet
Identification | Surface marking | E-File [AWG] SIS 600V 90C — AWM STYLE 3173 125C 600V XLPE VW-1 CSA CL1251 125C TEBAOFLEX
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
UL AWM 3173 / SIS Switchboard Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3173-sis-switchboard-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 44 Type SIS · UL 758 Style 3173 · CSA CL1251. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned or bare annealed copper | 7-strand Class B (for utility switchboard terminal blocks) or flexible 19/41/65-strand tinned copper (for hinged relay doors and motor leads) | ASTM B33 / B8 · UL 44 · UL 758
2 | 0.76 mm (30 mil) flame-retardant XLPE | Chemically or electron-beam cross-linked polyethylene meeting both UL 44 Type SIS and UL 758 Style 3173 | UL 44 Type SIS · UL 758 Style 3173
3 | Low-friction VW-1 switchboard finish | Smooth thermoset outer surface engineered for neat 90-degree bundle dressing and high-density terminal-block wiring in utility panels | UL 44 · CSA C22.2 No. 38 / No. 210
| UL 44 Type SIS / UL 3173 7-Strand Class B Tinned Copper (18–4/0 AWG) | Semi-rigid 7-strand tinned copper preferred by electric utilities for self-supporting relay-panel wiring
| UL 3173 / Type SIS / CSA CL1251 Flexible Stranded Tinned Copper (22–4/0 AWG) | Flexible 19/26/41/65-strand tinned copper for hinged breaker doors, motor leads and transformer coils

## Quality and supply
UL AWM 3173 / SIS Switchboard Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3173-sis-switchboard-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 44 Type SIS · UL 758 Style 3173 · CSA CL1251. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage test — 2.0 kV AC (50/60 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / ASTM (tinned copper) | Every manufactured length
Sample test | Flame propagation test — IEC 60332-1-2 / UL VW-1 / ISO 6722-1 | Per production batch
Type test | Insulation & sheath material physical properties — UL 44 Type SIS · UL 758 Style 3173 · CSA CL1251 | Type approval
Standard / approval | UL 44 Type SIS · UL 758 Style 3173 · CSA CL1251
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | [AWG] SIS 600V 90C — AWM 3173 125C 600V XLPE VW-1 CSA CL1251 TEBAOFLEX
Supply | Delivery form: Export wooden drums, reels or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums or spools with sealed ends
Supply | Conductor / colour options: Custom core counts, stripe combinations or cut harnesses on request