## Request a quote
Request a quotation for UL AWM 3265 / 3266
Application engineer · 125 °C XLPE & electronic wires
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ul-awm-3265-3266-cross-linked-hook-up-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
UL AWM 3265 / 3266 Cross-Linked Hook-Up Wire – Dimensions & weights (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3265-3266-cross-linked-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 3265 (150 V) & Style 3266 (300 V) · CSA CL1252. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² / AWG | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| UL 3265 150V 28 AWG (7/36) | 28 AWG (0.08 mm²) | 28 | 0.8 | 0.9 | 0 | 1 | 3 | UL AWM 3265 — 150 V 125 °C 10-mil Cross-Linked XLPE (28–18 AWG)
| UL 3265 150V 26 AWG (7/34) | 26 AWG (0.13 mm²) | 26 | 0.9 | 1 | 1 | 2 | 3 | UL AWM 3265 — 150 V 125 °C 10-mil Cross-Linked XLPE (28–18 AWG)
| UL 3265 150V 24 AWG (7/32) | 24 AWG (0.20 mm²) | 24 | 1 | 1.1 | 2 | 3 | 3 | UL AWM 3265 — 150 V 125 °C 10-mil Cross-Linked XLPE (28–18 AWG)
| UL 3265 150V 22 AWG (7/30) | 22 AWG (0.33 mm²) | 22 | 1.2 | 1.3 | 3 | 4 | 4 | UL AWM 3265 — 150 V 125 °C 10-mil Cross-Linked XLPE (28–18 AWG)
| UL 3265 150V 20 AWG (7/28) | 20 AWG (0.52 mm²) | 20 | 1.4 | 1.5 | 5 | 6 | 4 | UL AWM 3265 — 150 V 125 °C 10-mil Cross-Linked XLPE (28–18 AWG)
| UL 3265 150V 18 AWG (19/30) | 18 AWG (0.82 mm²) | 18 | 1.6 | 1.8 | 7 | 9 | 5 | UL AWM 3265 — 150 V 125 °C 10-mil Cross-Linked XLPE (28–18 AWG)
| UL 3266 300V 28 AWG (7/36) | 28 AWG (0.08 mm²) | 28 | 1.1 | 1.2 | 0 | 2 | 4 | UL AWM 3266 — 300 V 125 °C 16-mil Cross-Linked XLPE (28–16 AWG)
| UL 3266 300V 26 AWG (7/34) | 26 AWG (0.13 mm²) | 26 | 1.2 | 1.3 | 1 | 3 | 4 | UL AWM 3266 — 300 V 125 °C 16-mil Cross-Linked XLPE (28–16 AWG)
| UL 3266 300V 24 AWG (7/32) | 24 AWG (0.20 mm²) | 24 | 1.3 | 1.4 | 2 | 4 | 4 | UL AWM 3266 — 300 V 125 °C 16-mil Cross-Linked XLPE (28–16 AWG)
| UL 3266 300V 22 AWG (7/30) | 22 AWG (0.33 mm²) | 22 | 1.5 | 1.6 | 3 | 5 | 5 | UL AWM 3266 — 300 V 125 °C 16-mil Cross-Linked XLPE (28–16 AWG)
| UL 3266 300V 20 AWG (7/28) | 20 AWG (0.52 mm²) | 20 | 1.7 | 1.8 | 5 | 7 | 5 | UL AWM 3266 — 300 V 125 °C 16-mil Cross-Linked XLPE (28–16 AWG)
| UL 3266 300V 18 AWG (19/30) | 18 AWG (0.82 mm²) | 18 | 1.9 | 2 | 7 | 10 | 6 | UL AWM 3266 — 300 V 125 °C 16-mil Cross-Linked XLPE (28–16 AWG)
| UL 3266 300V 16 AWG (26/30) | 16 AWG (1.31 mm²) | 16 | 2.2 | 2.4 | 12 | 14 | 7 | UL AWM 3266 — 300 V 125 °C 16-mil Cross-Linked XLPE (28–16 AWG)
Dimensions and weights are typical values per UL 758 Style 3265 (150 V) & Style 3266 (300 V) · CSA CL1252. Minimum fixed bending radius shown is 3 × OD.

## Electrical & current ratings
UL AWM 3265 / 3266 Cross-Linked Hook-Up Wire – Electrical & current ratings (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3265-3266-cross-linked-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 3265 (150 V) & Style 3266 (300 V) · CSA CL1252. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single wire in air 30 °C, A | Multi-core bundle 30 °C, A
0.08 | 28 | 248 | 1.5 | 1.2
0.13 | 26 | 155 | 2.5 | 2.0
0.2 | 24 | 95.5 | 3.5 | 2.8
0.33 | 22 | 57.8 | 6.0 | 4.5
0.52 | 20 | 34.6 | 10 | 7
0.82 | 18 | 24 | 14 | 11
1.31 | 16 | 15.1 | 20 | 15
Current ratings at 30 °C ambient in free air. Apply temperature and bundle grouping factors per applicable equipment standard.

## Technical data
UL AWM 3265 / 3266 Cross-Linked Hook-Up Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3265-3266-cross-linked-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 3265 (150 V) & Style 3266 (300 V) · CSA CL1252. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 150 V / 300 V (UL 3265: 150 V · UL 3266: 300 V RMS)
Key data | Temp. rating | −55…+125 °C (UL 3265/3266 & CSA CL1252 (+125 °C))
Key data | Insulation wall | 0.25 / 0.41 mm (10 mil (UL 3265) · 16 mil (UL 3266))
Key data | Dielectric type | E-beam XLPE/XLPO (Thermoset cross-linked polyolefin)
Key data | Flame rating | Horiz. / VW-1 (UL Horizontal & VW-1 / CSA FT1 options)
Key data | Size range | 30–16 AWG (0.05–1.31 mm² · tinned copper)
Electrical | Rated voltage | 150 V RMS (UL Style 3265) · 300 V RMS (UL Style 3266 & CSA CL1252)
Electrical | Dielectric withstand voltage | 1500 V AC for 1 min · 3000 V AC spark test
Electrical | Dielectric constant (εr) | ≈ 2.3–2.6 (significantly lower capacitance than PVC)
Electrical | Max. DC conductor resistance (20 °C) | 28 AWG: ≤ 216 Ω/km · 24 AWG: ≤ 84.2 Ω/km · 22 AWG: ≤ 53.2 Ω/km · 20 AWG: ≤ 33.2 Ω/km · 18 AWG: ≤ 21.0 Ω/km · 16 AWG: ≤ 13.2 Ω/km
Thermal | Continuous temperature rating | −55 °C to +125 °C
Thermal | Short-circuit / solder heat | Thermoset cross-linked polymer resists +250 °C overload and 350 °C soldering irons without melting
Mechanical | Nominal insulation wall | UL 3265: 0.25 mm (10 mil) · UL 3266: 0.41 mm (16 mil)
Mechanical | Min. bending radius | 3 × overall diameter (fixed routing)
Resistance | Flame retardance | UL 758 Horizontal / UL 1581 VW-1 & CSA FT1
Resistance | Varnish & solvent resistance | Resists transformer baking varnishes, encapsulating resins, oils and cleaning solvents
Standards | UL AWM styles | UL 758 Style 3265 (150 V, 125 °C) & Style 3266 (300 V, 125 °C)
Standards | CSA certification | CSA C22.2 No. 210 Type CL1252 (125 °C, 300 V)
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant (halogen-free XLPO options available)
Identification | Standard stock colours | Black, White, Red, Blue, Yellow, Green, Brown, Orange, Violet & Grey
Identification | Surface marking | AWM STYLE 3265 150V OR 3266 300V 125C XLPE CSA CL1252 TEBAOFLEX
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
UL AWM 3265 / 3266 Cross-Linked Hook-Up Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3265-3266-cross-linked-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 3265 (150 V) & Style 3266 (300 V) · CSA CL1252. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded or solid tinned copper | Stranded (7/38 to 26/30) or solid tinned annealed copper per ASTM B33 (30 AWG to 16 AWG) | ASTM B33 · UL 758
2 | 125 °C cross-linked polyolefin (XLPE) | 0.25 mm (10 mil, UL 3265) or 0.41 mm (16 mil, UL 3266) electron-beam irradiated cross-linked polyethylene / polyolefin | UL 758 Style 3265 / 3266
3 | Thermoset flame-retardant XLPO skin | Non-melting, shrinkback-free surface available in standard flame-retardant or low-smoke halogen-free (LSZH) XLPO | UL 1581 · CSA C22.2 No. 210 CL1252
| UL AWM 3265 · CSA CL1252 (150 V, 125 °C, 0.25 mm / 10-mil XLPE) | Ultra-thin-wall 125 °C cross-linked polyolefin wire for compact sensor, coil and PCB harnesses
| UL AWM 3266 · CSA CL1252 (300 V, 125 °C, 0.41 mm / 16-mil XLPE) | 300 V 16-mil 125 °C cross-linked polyolefin wire for power supplies, appliances and Class B coils

## Quality and supply
UL AWM 3265 / 3266 Cross-Linked Hook-Up Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3265-3266-cross-linked-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 3265 (150 V) & Style 3266 (300 V) · CSA CL1252. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage test — 1.5 kV AC (50/60 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / ASTM (tinned copper) | Every manufactured length
Sample test | Flame propagation test — IEC 60332-1-2 / UL VW-1 / ISO 6722-1 | Per production batch
Type test | Insulation & sheath material physical properties — UL 758 Style 3265 (150 V) & Style 3266 (300 V) · CSA CL1252 | Type approval
Standard / approval | UL 758 Style 3265 (150 V) & Style 3266 (300 V) · CSA CL1252
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | AWM STYLE 3265/3266 125C XLPE CSA CL1252 TEBAOFLEX
Supply | Delivery form: Export wooden drums, reels or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums or spools with sealed ends
Supply | Conductor / colour options: Custom core counts, stripe combinations or cut harnesses on request