## Request a quote
Request a quotation for UL AWM 3271
Application engineer · UL motor lead & transformer wires
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ul-awm-3271-cross-linked-equipment-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
UL AWM 3271 Cross-Linked Equipment Wire – Dimensions & weights (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3271-cross-linked-equipment-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 3271 · CSA C22.2 No. 210 CL1251. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² / AWG | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| UL 3271 22 AWG (7/30) | 22 AWG (0.33 mm²) | 22 | 2.2 | 2.4 | 3 | 8 | 9 | 600 V 125 °C XLPE Equipment & Coil Leads (UL 3271, 22–10 AWG, 30-mil wall)
| UL 3271 20 AWG (10/30) | 20 AWG (0.52 mm²) | 20 | 2.3 | 2.5 | 5 | 10 | 10 | 600 V 125 °C XLPE Equipment & Coil Leads (UL 3271, 22–10 AWG, 30-mil wall)
| UL 3271 18 AWG (16/30) | 18 AWG (0.82 mm²) | 18 | 2.6 | 2.8 | 7 | 13 | 11 | 600 V 125 °C XLPE Equipment & Coil Leads (UL 3271, 22–10 AWG, 30-mil wall)
| UL 3271 16 AWG (26/30) | 16 AWG (1.31 mm²) | 16 | 2.9 | 3.1 | 12 | 19 | 12 | 600 V 125 °C XLPE Equipment & Coil Leads (UL 3271, 22–10 AWG, 30-mil wall)
| UL 3271 14 AWG (41/30) | 14 AWG (2.08 mm²) | 14 | 3.2 | 3.5 | 20 | 27 | 14 | 600 V 125 °C XLPE Equipment & Coil Leads (UL 3271, 22–10 AWG, 30-mil wall)
| UL 3271 12 AWG (65/30) | 12 AWG (3.31 mm²) | 12 | 3.7 | 4 | 31 | 40 | 16 | 600 V 125 °C XLPE Equipment & Coil Leads (UL 3271, 22–10 AWG, 30-mil wall)
| UL 3271 10 AWG (105/30) | 10 AWG (5.26 mm²) | 10 | 4.3 | 4.7 | 50 | 61 | 19 | 600 V 125 °C XLPE Equipment & Coil Leads (UL 3271, 22–10 AWG, 30-mil wall)
| UL 3271 8 AWG (133/29) | 8 AWG (8.37 mm²) | 8 | 5.9 | 6.4 | 80 | 104 | 26 | 600 V 125 °C XLPE Heavy Motor & Inverter Leads (UL 3271, 8–4 AWG)
| UL 3271 6 AWG (133/27) | 6 AWG (13.3 mm²) | 6 | 7.5 | 8.1 | 127 | 165 | 32 | 600 V 125 °C XLPE Heavy Motor & Inverter Leads (UL 3271, 8–4 AWG)
| UL 3271 4 AWG (133/25) | 4 AWG (21.2 mm²) | 4 | 8.7 | 9.5 | 203 | 252 | 38 | 600 V 125 °C XLPE Heavy Motor & Inverter Leads (UL 3271, 8–4 AWG)
Dimensions and weights are typical values per UL 758 Style 3271 · CSA C22.2 No. 210 CL1251. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
UL AWM 3271 Cross-Linked Equipment Wire – Electrical & current ratings (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3271-cross-linked-equipment-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 3271 · CSA C22.2 No. 210 CL1251. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single wire in air 30 °C, A | Multi-core bundle 30 °C, A
0.33 | 22 | 57.8 | 6.0 | 4.5
0.52 | 20 | 34.6 | 10 | 7
0.82 | 18 | 24 | 14 | 11
1.31 | 16 | 15.1 | 20 | 15
2.08 | 14 | 9.8 | 27 | 21
3.31 | 12 | 6.2 | 36 | 27
5.26 | 10 | 3.88 | 50 | 36
8.37 | 8 | 2.42 | 68 | 48
13.3 | 6 | 1.48 | 92 | 65
21.2 | 4 | 0.92 | 125 | 88
Current ratings at 30 °C ambient in free air. Apply temperature and bundle grouping factors per applicable equipment standard.

## Technical data
UL AWM 3271 Cross-Linked Equipment Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3271-cross-linked-equipment-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 3271 · CSA C22.2 No. 210 CL1251. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 600 V RMS (UL AWM Style 3271 & CSA CL1251)
Key data | Temp. rating | −55…+125 °C (Class B (130 °C) motor/transformer lead)
Key data | Insulation wall | 0.76 mm (30 mil) (30 mil (26–10 AWG) · 45–60 mil (8–2 AWG))
Key data | Dielectric type | Thermoset XLPE (Thermoset e-beam cross-linked polyolefin)
Key data | Flame rating | Horizontal / FT2 (UL Horizontal & VW-1 / CSA FT1 options)
Key data | Size range | 26–2 AWG (0.13–33.6 mm² · stranded tinned Cu)
Electrical | Rated voltage | 600 V RMS
Electrical | Dielectric withstand voltage | 2000 V AC for 1 min · 6000 V AC spark test
Electrical | Max. DC conductor resistance (20 °C) | 18 AWG: ≤ 21.0 Ω/km · 16 AWG: ≤ 13.2 Ω/km · 14 AWG: ≤ 8.28 Ω/km · 12 AWG: ≤ 5.21 Ω/km · 10 AWG: ≤ 3.28 Ω/km · 8 AWG: ≤ 2.06 Ω/km
Thermal | Continuous temperature rating | −55 °C to +125 °C (compatible with Class B 130 °C insulation systems)
Thermal | Baking & overload endurance | Withstands 160 °C varnish bake cycles and +250 °C short-circuit temperatures without melting or splitting
Mechanical | Nominal insulation wall | 26–10 AWG: 0.76 mm (30 mil) · 8 AWG: 1.14 mm (45 mil) · 6–2 AWG: 1.52 mm (60 mil)
Mechanical | Min. bending radius | 4 × overall diameter (fixed routing)
Resistance | Flame retardance | UL 758 Horizontal / FT2 (VW-1 / CSA FT1 flame-retardant grades available)
Resistance | Varnish, oil & solvent resistance | Resistant to polyester/epoxy impregnating varnishes, mineral oil, xylene and toluene
Standards | UL AWM style | UL 758 Appliance Wiring Material Style 3271 (600 V, 125 °C)
Standards | CSA certification | CSA C22.2 No. 210 Type CL1251 (600 V, 125 °C) & CSA AWM I A/B
Standards | Companion multi-ratings | Often dual/triple-marked with UL 3173, UL 3289 and CSA CL1251
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Standard stock colours | Black, White, Red, Blue, Yellow, Green, Brown, Orange, Violet & Grey
Identification | Surface marking | AWM STYLE 3271 125C 600V XLPE [AWG] CSA CL1251 125C 600V TEBAOFLEX
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
UL AWM 3271 Cross-Linked Equipment Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3271-cross-linked-equipment-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 3271 · CSA C22.2 No. 210 CL1251. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible stranded tinned copper | Fine-stranded tinned annealed copper (26 AWG to 2 AWG) per ASTM B33 for corrosion-free crimping, brazing and varnish baking | ASTM B33 · UL 758
2 | 0.76 mm (30 mil) 125 °C XLPE dielectric | Electron-beam or chemically cross-linked polyethylene / polyolefin (0.76 mm on 26–10 AWG; 1.14 mm on 8 AWG; 1.52 mm on 6–2 AWG) | UL 758 Style 3271
3 | Varnish- & crush-resistant XLPO finish | Thermoset surface that withstands coil lacing pressure, impregnating varnishes and 150–165 °C baking ovens | UL 758 · CSA C22.2 No. 210 CL1251
| UL AWM 3271 · CSA CL1251 Control & Coil Leads (26–10 AWG, 30-mil wall) | 600 V 125 °C XLPE lead wire for fractional-HP motors, control transformers and appliance harnesses
| UL AWM 3271 · CSA CL1251 Power & Stator Leads (8–2 AWG, 45/60-mil wall) | Heavy-gauge flexible tinned copper XLPE power leads for industrial motors, generators and inverters

## Quality and supply
UL AWM 3271 Cross-Linked Equipment Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-awm-3271-cross-linked-equipment-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 758 Style 3271 · CSA C22.2 No. 210 CL1251. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage test — 2.0 kV AC (50/60 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / ASTM (tinned copper) | Every manufactured length
Sample test | Flame propagation test — IEC 60332-1-2 / UL VW-1 / ISO 6722-1 | Per production batch
Type test | Insulation & sheath material physical properties — UL 758 Style 3271 · CSA C22.2 No. 210 CL1251 | Type approval
Standard / approval | UL 758 Style 3271 · CSA C22.2 No. 210 CL1251
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | AWM STYLE 3271 125C 600V XLPE [AWG] CSA CL1251 TEBAOFLEX
Supply | Delivery form: Export wooden drums, reels or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums or spools with sealed ends
Supply | Conductor / colour options: Custom core counts, stripe combinations or cut harnesses on request