## Request a quote
Request a quotation for VFD Mining Power 2 kV
Application engineer · North American VFD mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/vfd-mining-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
VFD Mining Power Cable (2,000 V · 3P+3G+GC) – Sizes & dimensions · 2 kV VFD (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/vfd-mining-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 · CSA C22.2 No. 96. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Power cores 3 × AWG/kcmil | Grounds (3) AWG/kcmil | Ground-check pilot | Jacket in | Jacket mm | Nominal OD in | Nominal OD mm | Weight ≈ lb/kft | Mass ≈ kg/km | Ampacity A (40 °C)
| VFD 2 kV · 3 × 2 AWG | 3 × 8 | 1 × GC (≥14 AWG) | 0.155 | 3.9 | 1.43 | 36.3 | 1790 | 2664 | 159
| VFD 2 kV · 3 × 1 AWG | 3 × 7 | 1 × GC (≥14 AWG) | 0.17 | 4.3 | 1.64 | 41.7 | 2150 | 3200 | 184
| VFD 2 kV · 3 × 1/0 AWG | 3 × 6 | 1 × GC (≥14 AWG) | 0.17 | 4.3 | 1.74 | 44.2 | 2550 | 3795 | 211
| VFD 2 kV · 3 × 2/0 AWG | 3 × 5 | 1 × GC (≥14 AWG) | 0.19 | 4.8 | 1.89 | 48 | 3100 | 4613 | 243
| VFD 2 kV · 3 × 3/0 AWG | 3 × 4 | 1 × GC (≥14 AWG) | 0.19 | 4.8 | 2.01 | 51.1 | 4050 | 6027 | 279
| VFD 2 kV · 3 × 4/0 AWG | 3 × 3 | 1 × GC (≥14 AWG) | 0.22 | 5.6 | 2.17 | 55.1 | 4390 | 6533 | 321
| VFD 2 kV · 3 × 250 kcmil | 3 × 3 | 1 × GC (≥14 AWG) | 0.22 | 5.6 | 2.4 | 61 | 5950 | 8855 | 355
| VFD 2 kV · 3 × 350 kcmil | 3 × 1 | 1 × GC (≥14 AWG) | 0.235 | 6 | 2.68 | 68.1 | 7840 | 11667 | 435
| VFD 2 kV · 3 × 500 kcmil | 3 × 1/0 | 1 × GC (≥14 AWG) | 0.265 | 6.7 | 3.03 | 77 | 9730 | 14480 | 536
Ampacity calculated at 90 °C conductor temperature and 40 °C ambient air; apply reel correction factors (1 layer: 0.85, 2: 0.65, 3: 0.45, 4: 0.35) when wound on drums.
Each cable includes 3 green-insulated grounding conductors and 1 yellow-insulated ground-check conductor under an overall foil + tinned copper braid shield.

## Technical data
VFD Mining Power Cable (2,000 V · 3P+3G+GC) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/vfd-mining-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 · CSA C22.2 No. 96. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 2,000 V (PWM inverter spike rated)
Key data | Core arrangement | 3P + 3G + 1GC (3 phase + 3 ground + 1 GC)
Key data | EMC shield | Foil + Cu braid (100 % Al/Mylar + Cu braid)
Key data | Size range | 2 AWG–500 kcmil (9 sizes · 159 to 536 A)
Key data | Max. conductor T | +90 °C (Type II EPDM/EPR · −40 °C)
Key data | Min. bend radius | 8 × OD (Shielded 2 kV trailing/reeling)
Electrical | Rated voltage | 2,000 V AC (designed for PWM inverter voltage spikes up to 2 kV class)
Electrical | Ampacity range | 159 to 536 A (90 °C conductor, 40 °C ambient in free air)
Electrical | Reel derating factors | 1 layer: × 0.85 · 2 layers: × 0.65 · 3 layers: × 0.45 · 4 layers: × 0.35
Electrical | Overall EMC shield | 100 % coverage aluminum/polyester foil tape + overall tinned copper wire braid (≥ 85 % braid coverage)
Electrical | Symmetrical grounds & pilot | Three green-insulated tinned copper grounds (3 × 8 AWG to 3 × 1/0 AWG) + central yellow ground-check (≥ 14 AWG)
Thermal | Max. continuous conductor temp. | +90 °C (Type II EPDM / EPR)
Thermal | Min. operating temperature | −40 °C
Thermal | Emergency overload & short-circuit | +130 °C overload · +250 °C short-circuit
Mechanical | Min. bending radius | 8 × OD (shielded 2 kV portable power cable per ICEA S-75-381)
Mechanical | Conductor stranding | Extra-flexible rope-lay stranded annealed tinned copper per ASTM B172 & ASTM B33
Mechanical | Outer jacket wall | Reinforced mold-cured thermoset CPE jacket (0.155 to 0.265 in / 3.9 to 6.7 mm nominal wall)
Resistance | Flame retardance | MSHA 30 CFR Part 7 flame resistance · CSA C22.2 No. 96 FT4
Resistance | Oil, chemical & ozone | Ozone-resistant Type II EPDM insulation + oil-, acid- and abrasion-resistant mold-cured CPE jacket
Resistance | Water & sunlight | 90 °C wet/dry rated for surface and underground mining VFD installations
Standards | Construction standard | ICEA S-75-381 / NEMA WC 58 · CSA C22.2 No. 96
Standards | Conductor standard | ASTM B172 & ASTM B33 (extra-flexible tinned copper)
Standards | Manufacturing tolerance | ±5 % on nominal outside diameter
Identification | Phase & ground colours | Phases: Black, White, Red · Grounds (3): Green · Ground-check (1): Yellow
Identification | Outer jacket | Black reinforced mold-cured thermoset CPE
Identification | Configuration code | 3 Power + 3 Symmetrical Grounds + 1 Ground-Check · Braid + Foil Shield (2,000 V)

## Construction
VFD Mining Power Cable (2,000 V · 3P+3G+GC) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/vfd-mining-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 · CSA C22.2 No. 96. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase conductors (3) | Extra-flexible rope-lay stranded tinned copper | ASTM B172 & ASTM B33
2 | Phase insulation | 90 °C Type II EPDM (EPR) ozone-resistant thermoset elastomer (2,000 V wall) | ICEA S-75-381
3 | Central ground-check pilot (1) | Central flexible tinned copper ground-check conductor with yellow insulation (interstitial option ≥ 14 AWG)
4 | Symmetrical grounds (3) | Three flexible rope-lay tinned copper grounding conductors with green insulation in the three outer interstices | Balanced 120° ground return
5 | Foil shield (100 % coverage) | Aluminum / polyester laminate tape over cabled core assembly (100 % high-frequency coverage)
6 | Overall copper braid shield | Overall tinned copper wire braid shield over foil tape
7 | Outer jacket | Reinforced mold-cured thermosetting chlorinated polyethylene (CPE) jacket, black (3.9 to 6.7 mm wall) | ICEA S-75-381 / CSA C22.2 No. 96
| Center Ground-Check (3P + 3G + Center GC) | Central yellow ground-check conductor surrounded by 3 phase cores and 3 interstitial green grounds for true 120° electromagnetic symmetry
| Interstitial Ground-Check Option | Non-center yellow ground-check conductor (minimum 14 AWG) when specified by connector or coupler geometry

## Quality and supply
VFD Mining Power Cable (2,000 V · 3P+3G+GC) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/vfd-mining-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ICEA S-75-381 / NEMA WC 58 · CSA C22.2 No. 96. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | In-line spark & high-voltage AC dielectric test — 100 % spark test and routine AC withstand test for 2,000 V class per ICEA S-75-381 | Every shipping length
Routine test | Phase, ground, pilot & shield continuity / DC resistance — Verified on all 3 phase cores, 3 grounds, 1 GC pilot and overall braid+foil shield | Every shipping length
Sample test | Vertical flame resistance test — Self-extinguishing per MSHA 30 CFR Part 7 and CSA C22.2 No. 96 FT4 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · VFD POWER CABLE · 2000V · 90C · 3/C [size] + 3G + GC · SHIELDED · EPDM/CPE · ICEA S-75-381
Supply | Delivery form: Export seaworthy fumigated wooden reels matched to 8 × OD minimum bend radius
Supply | Lengths: Custom cut-to-length reels per VFD motor feeder schedule
Supply | Certificate: EN 10204 3.1 factory inspection certificate per reel
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None