## Request a quote
Request a quotation for VPL Power-Limiting Heating Cable
Application engineer · industrial heat-tracing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/vpl-high-temperature-coiled-resistor-alloy-power-limiting-industrial-heat-tracing-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
VPL Power-Limiting Heating Cable – Power output, thermal ratings, zone length & dimensions (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/vpl-high-temperature-coiled-resistor-alloy-power-limiting-industrial-heat-tracing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | VPL model designation | Rated Vac | Output @10°C W/m | Output @150°C W/m | Max maintain °C | Max exposure °C | T-class (IEC) | Zone pitch m | Max circuit m | Width × Thick. mm | Mass ≈ kg/km
| 5VPL1-CT · 120 V | 120 Vac | 15 | 10 | 235 | 260 | T3 / T2 | 0.6 | 115 | 11.7 × 7.6 | 210
| 10VPL1-CT · 120 V | 120 Vac | 33 | 21 | 220 | 260 | T3 / T2 | 0.5 | 80 | 11.7 × 7.6 | 212
| 15VPL1-CT · 120 V | 120 Vac | 49 | 30 | 200 | 260 | T3 / T2 | 0.45 | 65 | 11.7 × 7.6 | 215
| 20VPL1-CT · 120 V | 120 Vac | 65 | 38 | 175 | 260 | T2 | 0.45 | 55 | 11.7 × 7.6 | 218
| 5VPL2-CT · 240 V | 240 Vac | 15 | 10 | 235 | 260 | T3 / T2 | 0.9 | 230 | 11.7 × 7.6 | 210
| 10VPL2-CT · 240 V | 240 Vac | 33 | 21 | 220 | 260 | T3 / T2 | 0.75 | 160 | 11.7 × 7.6 | 212
| 15VPL2-CT · 240 V | 240 Vac | 49 | 30 | 200 | 260 | T3 / T2 | 0.65 | 130 | 11.7 × 7.6 | 215
| 20VPL2-CT · 240 V | 240 Vac | 65 | 38 | 175 | 260 | T2 | 0.6 | 110 | 11.7 × 7.6 | 218
| 5VPL4-CT · 480 V | 480 Vac | 15 | 10 | 235 | 260 | T3 / T2 | 1.1 | 440 | 11.7 × 7.6 | 212
| 10VPL4-CT · 480 V | 480 Vac | 33 | 21 | 220 | 260 | T3 / T2 | 1 | 310 | 11.7 × 7.6 | 214
| 15VPL4-CT · 480 V | 480 Vac | 49 | 30 | 200 | 260 | T3 / T2 | 0.9 | 250 | 11.7 × 7.6 | 216
| 20VPL4-CT · 480 V | 480 Vac | 65 | 38 | 175 | 260 | T2 | 0.8 | 215 | 11.7 × 7.6 | 220
All VPL cables use 3.3 mm² (12 AWG) nickel-plated copper bus wires; 240 V models operate across 200–277 Vac and 480 V models operate across 380–480 Vac with voltage-adjusted output.

## Linear output vs pipe temperatu
VPL Power-Limiting Heating Cable – Linear output vs pipe temperature & breaker sizing (240 Vac & 480 Vac) (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/vpl-high-temperature-coiled-resistor-alloy-power-limiting-industrial-heat-tracing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
VPL model | W/m @ +10 °C | W/m @ +100 °C | W/m @ +200 °C | 20 A breaker max m | 32 A breaker max m | 40 A breaker max m
5VPL2-CT (240 V) | 15 | 12 | 8 | 195 | 230 | 230
10VPL2-CT (240 V) | 33 | 25 | 17 | 95 | 150 | 160
15VPL2-CT (240 V) | 49 | 36 | 24 | 65 | 105 | 130
20VPL2-CT (240 V) | 65 | 46 | 28 | 50 | 80 | 100
10VPL4-CT (480 V) | 33 | 25 | 17 | 190 | 300 | 310
15VPL4-CT (480 V) | 49 | 36 | 24 | 130 | 210 | 250
20VPL4-CT (480 V) | 65 | 46 | 28 | 100 | 160 | 200
Notice how VPL retains 60–65 % of its +10 °C power output at +150 °C (unlike polymeric PTC tapes that taper steeply above +110 °C) while still limiting cold-start inrush and hot-spot temperature.

## Technical data
VPL Power-Limiting Heating Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/vpl-high-temperature-coiled-resistor-alloy-power-limiting-industrial-heat-tracing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Linear output | 15–65 W/m @10°C (5VPL 15 · 10VPL 33 · 15VPL 49 · 20VPL 65)
Key data | Maintain temp. | Up to +235 °C (High-wattage output at +150 to +235 °C)
Key data | Max. exposure T | +260 °C cont. (Continuous +260 °C power-off steam purge)
Key data | Supply voltage | 120 / 240 / 480V (100–130 V, 200–277 V & 380–480 V AC)
Key data | Bus conductors | 2 × 3.3 mm² (12 AWG Ni-plated Cu for long circuits)
Key data | Min. bend radius | 20 mm @ −60 °C (Flexible fluoropolymer construction)
Electrical | Rated supply voltage | 120 Vac (-1), 208–277 Vac (-2), 480 Vac (-4)
Electrical | Nominal output @ 10 °C | 15, 33, 49 & 65 W/m (5, 10, 15 & 20 W/ft)
Electrical | PTC alloy power taper | Metallic PTC resistor lowers W/m as T rises
Electrical | Dielectric withstand | 2.5 kV AC RMS for 1 min (bus to earth braid)
Thermal | Max. maintain temp. | Up to +235 °C (5VPL) · +175 °C (20VPL)
Thermal | Max. exposure temp. | +260 °C continuous (power off / steam purge)
Thermal | Min. installation T | −60 °C (fluoropolymer inner & outer jackets)
Thermal | Temperature class | T4 (+135 °C), T3 (+200 °C) & T2 (+300 °C)
Mechanical | Bus wire cross-section | 2 × 3.3 mm² (12 AWG) nickel-plated copper
Mechanical | Heating zone length | 0.45 m to 1.1 m between nodal bus contacts
Mechanical | Min. bending radius | 20 mm at −60 °C (do not bend on contact node)
Mechanical | Single-overlap safety | PTC alloy coil permits single valve overlap
Resistance | Flame retardance | IEC 60332-1-2 & IEEE 515 vertical flame
Resistance | Chemical & oil resistance | -CT fluoropolymer resists acids, bases & oils
Resistance | Steam-purge endurance | Withstands 300 psig (+215 to +260 °C) steam
Resistance | Moisture & UV | IP66/IP67 sealed system; UV-immune PFA sheath
Standards | Applicable standards | IEC/IEEE 60079-30-1, IEC 62395-1 & IEEE 515
Standards | Conductor standard | ASTM B355 Class 2/27 nickel-plated copper
Standards | Earth fault device | 30 mA RCD / GFPD required per IEC 60079-30-2
Standards | RoHS & REACH | RoHS 2011/65/EU & REACH compliant materials
Identification | Sheath colour code | Red-orange high-temp fluoropolymer (-CT)
Identification | Nodal contact marks | Printed / indented node marks every 0.45–1.1m
Identification | Surface legend | TEBAOFLEX · [5–20VPL] · [Vac] · +260°C · T2/T3
Identification | Customs tariff (HS) | 8544.49 (or 8516.80 electric heating cables)

## Construction
VPL Power-Limiting Heating Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/vpl-high-temperature-coiled-resistor-alloy-power-limiting-industrial-heat-tracing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 12 AWG (3.3 mm²) nickel-plated copper bus wires | 2 × 3.3 mm² (12 AWG) stranded nickel-plated copper bus conductors for low voltage drop and long circuit runs up to 480 Vac | ASTM B355 / IEC 60228
2 | High-temperature fluoropolymer bus insulation | Melt-extruded high-temperature fluoropolymer (PFA/FEP) primary bus dielectric with staggered nodal contact windows | IEC 60079-30-1 / IEEE 515
3 | Coiled PTC metallic resistor heating element | Positive-temperature-coefficient (PTC) metallic alloy heating wire coiled around the bus cores to reduce output as temperature rises | IEC 60079-30-1 / IEEE 515
4 | Fluoropolymer inner dielectric barrier jacket | Extruded high-temperature fluoropolymer inner jacket isolating the coiled PTC alloy heating zones from the metallic braid | IEC 60079-30-1
5 | Tinned / nickel-plated copper protective braid | Closely woven tinned or nickel-plated copper braid (≥ 70 % coverage, < 10 Ω/km) providing continuous earth path and mechanical armour | IEC 60079-30-1 Clause 4.4
6 | High-temperature fluoropolymer (-CT) outer jacket | Extruded PFA/fluoropolymer outer overjacket rated for +260 °C continuous power-off exposure and corrosive chemical service | IEC 60079-30-1 / IEEE 515
| VPL1-CT · 120 Vac Service (5VPL1, 10VPL1, 15VPL1, 20VPL1) | 100–130 Vac · 15 to 65 W/m @ 10 °C · Maintain up to +235 °C · Exposure +260 °C · 12 AWG NiCu bus + coiled PTC alloy + fluoropolymer jacket
| VPL2-CT · 240 Vac Service (5VPL2, 10VPL2, 15VPL2, 20VPL2) | 200–277 Vac · 15 to 65 W/m @ 10 °C · Maintain up to +235 °C · Exposure +260 °C · Standard industrial 230/240 V high-temp power-limiting series
| VPL4-CT · 480 Vac Service (5VPL4, 10VPL4, 15VPL4, 20VPL4) | 380–480 Vac · 15 to 65 W/m @ 10 °C · Maintain up to +235 °C · Exposure +260 °C · Extended circuit lengths up to 440 m on 400/480 V distribution

## Quality and supply
VPL Power-Limiting Heating Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/vpl-high-temperature-coiled-resistor-alloy-power-limiting-industrial-heat-tracing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage withstand test — 2.5 kV RMS AC for 1 min between 12 AWG bus conductors and metallic earth braid | Every reel
Routine test | Power-limiting PTC output & zone resistance check — Linear output at +10 °C and PTC resistance slope verified across coiled heating zones | Every reel
Sample test | −60 °C cold bend, 2 J impact & 1,500 N crush test — 20 mm cold mandrel flexing at −60 °C, impact and crush deformation per IEC 60079-30-1 | Production lot
Type test | 260 °C thermal endurance & single-overlap T-class test — Continuous +260 °C oven aging and stabilised sheath temperature test for T2/T3/T4 certification | Type qualification
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · [5VPL–20VPL] · [W/m @ 10°C] · [120V/240V/480V] · MAX EXP +260°C · IEC 60079-30-1 · NODE MARK
Supply | Delivery form: Continuous fluoropolymer-jacketed reels or cut circuits
Supply | Lengths: Field cut-to-length between nodal connection marks
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None