## Request a quote
Request a quotation for VSD EMC 3C+3E
Application engineer · EMC & VFD drive cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/vsd-emc-3c-3e-0-6-1kv-symmetrical-tri-earth-copper-tape-screened-drive-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
VSD EMC 3C+3E 0.6/1 kV Symmetrical Copper-Tape Drive Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/vsd-emc-3c-3e-0-6-1kv-symmetrical-tri-earth-copper-tape-screened-drive-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| VSD EMC 3C+3E 3×35 + 3×6 mm² | 3 × 35 mm² + 3 × 6 mm² (3E) | AS/NZS 1125 plain Cu | 26.8 | 1520 | 18 | 320 | VSD EMC 3C+3E Construction Schedule (-25 to +90 °C)
| VSD EMC 3C+3E 3×95 + 3×16 mm² | 3 × 95 mm² + 3 × 16 mm² (3E) | AS/NZS 1125 plain Cu | 39.2 | 3740 | 48 | 470 | VSD EMC 3C+3E Construction Schedule (-25 to +90 °C)
| VSD EMC 3C+3E 3×150 + 3×25 mm² | 3 × 150 mm² + 3 × 25 mm² (3E) | AS/NZS 1125 plain Cu | 47.5 | 5680 | 75 | 570 | VSD EMC 3C+3E Construction Schedule (-25 to +90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808.

## Electrical, optical & thermal p
VSD EMC 3C+3E 0.6/1 kV Symmetrical Copper-Tape Drive Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/vsd-emc-3c-3e-0-6-1kv-symmetrical-tri-earth-copper-tape-screened-drive-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 35 mm² + 3 × 6 mm² (3E) | 0.524 | 0.6/1 kV (158 A) | -25 to +90 °C
3 × 95 mm² + 3 × 16 mm² (3E) | 0.193 | 0.6/1 kV (285 A) | -25 to +90 °C
3 × 150 mm² + 3 × 25 mm² (3E) | 0.124 | 0.6/1 kV (365 A) | -25 to +90 °C
Every production length undergoes routine conductor DC resistance, high-voltage Spark/AC dielectric or OTDR continuity and dimensional verification.

## Technical data
VSD EMC 3C+3E 0.6/1 kV Symmetrical Copper-Tape Drive Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/vsd-emc-3c-3e-0-6-1kv-symmetrical-tri-earth-copper-tape-screened-drive-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (0.6/1 kV (1.2 kV max) VSD/VFD feeder)
Key data | Operating temp. | -25 to +90 °C (Continuous mining & industrial duty)
Key data | Min. bend radius | 12 × OD (Fixed installation / dynamic routing)
Key data | Core / conductor | 3×16–240 + 3×E (AS/NZS 1125 Cu + 3 symmetrical earths)
Key data | Outer protection | Cu-Tape + 5V-90 (100% copper tape + black 5V-90 PVC)
Key data | Standard | AS/NZS 5000.1 (AS/NZS 5000.1 / 1125 / 3808)
Electrical | Rated voltage / transmission duty | 0.6/1 kV (AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808)
Electrical | Core / conductor construction | Phase Conductors (3×95 mm²) — AS/NZS 1125 plain annealed copper (Class 2 standard or Class 5 flexible)
Electrical | Primary dielectric / buffering | X-90 XLPE Phase Insulation — 90 °C crosslinked polyethylene color-coded Red, White & Blue
Thermal | Continuous operating temperature | -25 to +90 °C (mining & industrial service)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Outer Sheath (Black 5V-90 PVC) — UV-stabilized, flame-retardant and oil-resistant black 5V-90 PVC jacket
Mechanical | Minimum bending radius | 12 × OD
Mechanical | Crush, impact & abrasion duty | Heavy-duty mining rock-cut, impact and tensile protection per AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808
Resistance | Flame retardancy & mine fire safety | Self-extinguishing / flame-retardant mining jacket per AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808
Resistance | Mine water, oil & chemical resistance | Resistant to acidic mine water, hydraulic oils and abrasion per AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808
Standards | Flame & environmental test standards | IEC 60332 / MSHA / EN 60794 / IEC 60228
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | VSD EMC 3C+3E
Identification | Sheath colour & metre marking | Continuous metre-marked black mining outer sheath
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
VSD EMC 3C+3E 0.6/1 kV Symmetrical Copper-Tape Drive Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/vsd-emc-3c-3e-0-6-1kv-symmetrical-tri-earth-copper-tape-screened-drive-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase Conductors (3×95 mm²) | AS/NZS 1125 plain annealed copper (Class 2 standard or Class 5 flexible)
2 | X-90 XLPE Phase Insulation | 90 °C crosslinked polyethylene color-coded Red, White & Blue
3 | Symmetrical Tri-Earth Cores (3×16 mm²) | Three Green/Yellow X-90 insulated split earths in phase interstices
4 | Black PVC Bedding & Copper Tape Screen | Extruded black PVC inner bedding + 100% helically lapped copper tape screen
5 | Outer Sheath (Black 5V-90 PVC) | UV-stabilized, flame-retardant and oil-resistant black 5V-90 PVC jacket
| VSD EMC 3C+3E — Standard Mining Execution | Built to AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808 with phase conductors (3×95 mm²) and outer sheath (black 5v-90 pvc)
| VSD EMC 3C+3E — Custom Drum Length & Gland Kit | Available in custom shaft/roadway drum lengths or pre-terminated assemblies
| VSD EMC 3C+3E — Routine & Flame Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & flame test report

## Quality and supply
VSD EMC 3C+3E 0.6/1 kV Symmetrical Copper-Tape Drive Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/vsd-emc-3c-3e-0-6-1kv-symmetrical-tri-earth-copper-tape-screened-drive-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808) — DC resistance at 20 °C / optical attenuation and outer diameter within AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808) — Zero dielectric breakdown and verified insulation resistance over full production length | Every manufactured drum length
Type test | Flame propagation, mechanical crush & thermal ageing qualification (AS/NZS 5000.1 / AS/NZS 1125 / AS/NZS 3808) — Verified flame retardancy, mechanical integrity and thermal endurance across -25 to +90 °C | Type qualification & periodic lot audit
Standard / approval | AS/NZS 5000.1 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX VSD EMC 3C+3E AS/NZS 5000.1 0.6/1 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel mine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shaft/reeling lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP