## Request a quote
Request a quotation for Vented Level-Sensor Cable
Application engineer · instrumentation & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/pur-sheathed-vented-capillary-tube-submersible-hydrostatic-level-transmitter-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Vented Level-Sensor Cable – Dimensions, vent ID & tensile ratings (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/pur-sheathed-vented-capillary-tube-submersible-hydrostatic-level-transmitter-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50288-7 / IEC 60794 / KTW-BWGL / ACS. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores, vent tube & jacket | Outer Ø mm | Vent ID mm | Weight ≈ kg/km | Tensile max N | Series
| VLC-PUR 2×0.50 + Vent | 2×0.50 mm² + 1.2 mm PA12 Vent · PUR | 7.2 | 1.2 | 64 | 1000 | Submersible Vented Capillary Hydrostatic Level Transmitter Cables
| VLC-PUR 4×0.34 + Vent | 4×0.34 mm² + 1.2 mm PA12 Vent · PUR | 7.5 | 1.2 | 72 | 1000 | Submersible Vented Capillary Hydrostatic Level Transmitter Cables
| VLC-PUR 6×0.25 + Vent | 6×0.25 mm² + 1.2 mm PA12 Vent · PUR | 7.8 | 1.2 | 78 | 1200 | Submersible Vented Capillary Hydrostatic Level Transmitter Cables
| VLC-FEP 4×0.34 + Vent | 4×0.34 mm² + 1.2 mm PTFE Vent · FEP | 7.4 | 1.2 | 92 | 1000 | Submersible Vented Capillary Hydrostatic Level Transmitter Cables
Outer diameter tolerance is held to ±0.15 mm for leak-tight compression in submersible transmitter Viton/EPDM seals.

## Technical data
Vented Level-Sensor Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/pur-sheathed-vented-capillary-tube-submersible-hydrostatic-level-transmitter-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50288-7 / IEC 60794 / KTW-BWGL / ACS. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Central vent tube | 1.0–1.5 mm ID (PA12 / PE kink-proof capillary)
Key data | Conductors | 2C to 6C + Scree (0.25 / 0.34 / 0.50 mm² tinned Cu)
Key data | Tensile rating | 500 to 1,200 N (Integrated para-aramid yarn)
Key data | Submersion depth | Up to 300 m H₂O (30 bar hydrostatic pressure)
Key data | Outer jacket | Polyether-PUR (Microbe & sewage resistant)
Key data | Operating temp. | -30 to +85 °C (FEP / TPE-E core insulation)
Electrical | Rated voltage | 300 V rms (4–20 mA / HART / RS-485 / SDI-12)
Electrical | Max. DC resistance @ 20 °C | 79.0 Ω/km (0.25) · 57.0 Ω/km (0.34) · 39.0 Ω/km (0.50 mm²)
Electrical | Insulation resistance | ≥ 1,000 MΩ·km @ 500 V DC
Electrical | Test voltage | 1,500 V AC rms (core-to-core & core-to-screen)
Thermal | Operating temp. (PUR / PE) | -30 °C to +85 °C (fixed submerged)
Thermal | Operating temp. (FEP chemical) | -40 °C to +105 °C
Thermal | Ice-formation resistance | Thick-wall PA12 tube resists surface frost pinch
Mechanical | Vent capillary dimensions | 1.2 mm ID × 2.4 mm OD (or 1.5 × 2.6 mm) PA12/PE tube
Mechanical | Max. tensile suspension load | 500 N working / 1,200 N breaking (para-aramid core)
Mechanical | Min. bend radius | 10 × OD without restricting airflow through vent tube
Resistance | Hydrostatic water depth | Up to 300 m water column (3.0 MPa / 30 bar) without tube collapse
Resistance | Microbial & sewage resist. | Polyether-PUR immune to bacterial hydrolysis, H₂S & grease
Resistance | Drinking water option | Available with KTW-BWGL / WRAS / ACS / NSF-61 PE jacket
Standards | Instrumentation construction | EN 50288-7 & IEC 60228 Class 5 tinned copper
Standards | Halogen-free & RoHS | IEC 60754-1 (PUR/PE) · 2011/65/EU RoHS 2 & REACH
Standards | Oil resistance | EN 60811-404 / DIN VDE 0282-10
Identification | Sheath colour | Black or Blue (Potable Water) with smooth gland-sealing surface
Identification | Customs tariff (HS) | 8544.4993
Identification | Core colour code | DIN 47100 (White, Brown, Green, Yellow, Grey, Pink)

## Construction
Vented Level-Sensor Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/pur-sheathed-vented-capillary-tube-submersible-hydrostatic-level-transmitter-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50288-7 / IEC 60794 / KTW-BWGL / ACS. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned copper conductors + central PA12/PE vent tube | 2 to 6 × Class 5 flexible tinned copper conductors (0.25, 0.34 or 0.50 mm²) helically laid around a central 1.0–1.5 mm ID × 2.3–2.6 mm OD Polyamide 12 (PA12) or HDPE capillary tube
2 | Hydrolysis-proof TPE-E / FEP primary core insulation | High-insulation-resistance Hytrel (TPE-E), PP or FEP fluoropolymer core insulation
3 | Para-aramid tensile yarns & non-hygroscopic bedding | High-modulus para-aramid roving spun around the core assembly + water-blocking polyester tape
4 | Tinned copper EMC braid screen + drain wire | ≥ 85 % optical coverage tinned copper wire braid + stranded tinned copper drain wire
5 | Submersible Polyether-PUR (or FEP /potable-water PE) jacket | Pressure-extruded Matte Black or Blue hydrolysis-, microbe- and oil-resistant Polyether Polyurethane (optional FEP or potable-water PE)
| VLC-PUR-2C050 (2 × 0.50 mm² + Vent + Aramid) | 2-wire 4–20 mA loop-powered submersible level transmitter cable (7.2 mm OD)
| VLC-PUR-4C034 (4 × 0.34 mm² + Vent + Aramid) | 4-core submersible level + Pt100 / RS-485 Modbus / SDI-12 transmitter cable (7.5 mm OD)
| VLC-FEP-6C025 (6 × 0.25 mm² + Vent · FEP Jacket) | All-fluoropolymer FEP outer jacketed vented level cable for aggressive chemical/leachate wells

## Quality and supply
Vented Level-Sensor Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/pur-sheathed-vented-capillary-tube-submersible-hydrostatic-level-transmitter-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50288-7 / IEC 60794 / KTW-BWGL / ACS. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % pneumatic vent-tube airflow & 3.0 bar pressure decay test — Unrestricted barometric airflow and zero capillary pinholes over full reel | Every manufactured reel
Routine test | 100 % 1.5 kV AC dielectric, IR & laser diameter concentricity check — Zero breakdown, IR ≥ 1,000 MΩ·km and OD circularity ≤ 0.15 mm | Every manufactured reel
Type test | 30 bar (300 m H₂O) hydrostatic crush & cable-clamp bend test — < 5 % airflow reduction under 30 bar external water pressure & 10 × OD clamp | Type qualification
Standard / approval | EN 50288-7 Compliant
Standard / approval | KTW / WRAS / NSF-61 Option
Standard / approval | RoHS 2 & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX SUBMERSIBLE VENTED LEVEL CABLE PUR + ARAMID
Supply | Delivery form: Fumigated wooden drums, steel reels or precision spools
Supply | Standard lengths: 500 m · 1000 m (or custom cut/spooled lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP