## Request a quote
Request a quotation for Vertical Mineshaft SIA
Application engineer · armoured mining power cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/vertical-mineshaft-sia-5kv-self-supporting-steel-interlocked-armour-drop-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
Vertical Mineshaft SIA 5 kV Self-Supporting Borehole Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/vertical-mineshaft-sia-5kv-self-supporting-steel-interlocked-armour-drop-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on CSA C22.2 No. 131 / CSA C68.10 / UL 1569. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| Vertical Mineshaft SIA 5 kV 3×2/0 AWG | 3 × 2/0 AWG + 3 Steel Messengers | Class B Cu + Galvanized Steel | 56.4 | 5420 | 85 | 675 | Vertical Mineshaft SIA Construction Schedule (-40 to +90 °C)
| Vertical Mineshaft SIA 5 kV 3×4/0 AWG | 3 × 4/0 AWG + 3 Steel Messengers | Class B Cu + Galvanized Steel | 63.8 | 7180 | 115 | 765 | Vertical Mineshaft SIA Construction Schedule (-40 to +90 °C)
| Vertical Mineshaft SIA 5 kV 3×350 kcmil | 3 × 350 kcmil + 3 Steel Messengers | Class B Cu + Galvanized Steel | 74.2 | 10450 | 160 | 890 | Vertical Mineshaft SIA Construction Schedule (-40 to +90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per CSA C22.2 No. 131 / CSA C68.10 / UL 1569.

## Electrical, optical & thermal p
Vertical Mineshaft SIA 5 kV Self-Supporting Borehole Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/vertical-mineshaft-sia-5kv-self-supporting-steel-interlocked-armour-drop-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on CSA C22.2 No. 131 / CSA C68.10 / UL 1569. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 2/0 AWG + 3 Steel Messengers | 0.261 | 5 kV 100%/133% (215 A) | -40 to +90 °C
3 × 4/0 AWG + 3 Steel Messengers | 0.164 | 5 kV 100%/133% (285 A) | -40 to +90 °C
3 × 350 kcmil + 3 Steel Messengers | 0.099 | 5 kV 100%/133% (395 A) | -40 to +90 °C
Every production length undergoes routine conductor DC resistance, high-voltage Spark/AC dielectric or OTDR continuity and dimensional verification.

## Technical data
Vertical Mineshaft SIA 5 kV Self-Supporting Borehole Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/vertical-mineshaft-sia-5kv-self-supporting-steel-interlocked-armour-drop-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on CSA C22.2 No. 131 / CSA C68.10 / UL 1569. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 5 kV (5 kV (600 V to 15 kV vertical drop))
Key data | Operating temp. | -40 to +90 °C (Continuous mining & industrial duty)
Key data | Min. bend radius | 12 × OD (Fixed installation / dynamic routing)
Key data | Core / conductor | 3×2 AWG–500 MCM (Class B bare Cu + 3 steel messengers)
Key data | Outer protection | SIA + FT4 Orange (Ribbed inner lock + SIA + FT4 PVC)
Key data | Standard | CSA C22.2 #131 (CSA C22.2 No. 131 / CSA C68.10 / UL 1569)
Electrical | Rated voltage / transmission duty | 5 kV (CSA C22.2 No. 131 / CSA C68.10 / UL 1569)
Electrical | Core / conductor construction | 5 kV Phase Conductors (3×2/0 AWG) — Stranded bare copper + semicon screens + 90 °C RW90 XLPE + copper tape shield
Electrical | Primary dielectric / buffering | Internal Steel Support Messengers — Individually PVC-jacketed high-tensile galvanized steel support cables
Thermal | Continuous operating temperature | -40 to +90 °C (mining & industrial service)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per CSA C22.2 No. 131 / CSA C68.10 / UL 1569
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | FT4 Low-Temp Outer Jacket — Sunlight-, oil- and -40 °C cold-impact resistant FT4 FR-PVC jacket
Mechanical | Minimum bending radius | 12 × OD
Mechanical | Crush, impact & abrasion duty | Heavy-duty mining rock-cut, impact and tensile protection per CSA C22.2 No. 131 / CSA C68.10 / UL 1569
Resistance | Flame retardancy & mine fire safety | Self-extinguishing / flame-retardant mining jacket per CSA C22.2 No. 131 / CSA C68.10 / UL 1569
Resistance | Mine water, oil & chemical resistance | Resistant to acidic mine water, hydraulic oils and abrasion per CSA C22.2 No. 131 / CSA C68.10 / UL 1569
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | CSA C22.2 No. 131 / CSA C68.10 / UL 1569
Standards | Flame & environmental test standards | IEC 60332 / MSHA / EN 60794 / IEC 60228
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | Vertical Mineshaft SIA
Identification | Sheath colour & metre marking | Continuous metre-marked orange mining outer sheath
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
Vertical Mineshaft SIA 5 kV Self-Supporting Borehole Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/vertical-mineshaft-sia-5kv-self-supporting-steel-interlocked-armour-drop-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on CSA C22.2 No. 131 / CSA C68.10 / UL 1569. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 5 kV Phase Conductors (3×2/0 AWG) | Stranded bare copper + semicon screens + 90 °C RW90 XLPE + copper tape shield
2 | Internal Steel Support Messengers | Individually PVC-jacketed high-tensile galvanized steel support cables
3 | Ribbed Anti-Slip Inner Jacket | Extruded FR-PVC inner jacket with longitudinal ribs locking core assembly
4 | Steel Interlocked Armour (SIA) | Galvanized steel interlocked armour mechanically engaged with inner ribs
5 | FT4 Low-Temp Outer Jacket | Sunlight-, oil- and -40 °C cold-impact resistant FT4 FR-PVC jacket
| Vertical Mineshaft SIA — Standard Mining Execution | Built to CSA C22.2 No. 131 / CSA C68.10 / UL 1569 with 5 kv phase conductors (3×2/0 awg) and ft4 low-temp outer jacket
| Vertical Mineshaft SIA — Custom Drum Length & Gland Kit | Available in custom shaft/roadway drum lengths or pre-terminated assemblies
| Vertical Mineshaft SIA — Routine & Flame Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & flame test report

## Quality and supply
Vertical Mineshaft SIA 5 kV Self-Supporting Borehole Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/vertical-mineshaft-sia-5kv-self-supporting-steel-interlocked-armour-drop-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on CSA C22.2 No. 131 / CSA C68.10 / UL 1569. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (CSA C22.2 No. 131 / CSA C68.10 / UL 1569) — DC resistance at 20 °C / optical attenuation and outer diameter within CSA C22.2 No. 131 / CSA C68.10 / UL 1569 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (CSA C22.2 No. 131 / CSA C68.10 / UL 1569) — Zero dielectric breakdown and verified insulation resistance over full production length | Every manufactured drum length
Type test | Flame propagation, mechanical crush & thermal ageing qualification (CSA C22.2 No. 131 / CSA C68.10 / UL 1569) — Verified flame retardancy, mechanical integrity and thermal endurance across -40 to +90 °C | Type qualification & periodic lot audit
Standard / approval | CSA C22.2 #131 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX Vertical Mineshaft SIA CSA C22.2 #131 5 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel mine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shaft/reeling lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP