## Request a quote
Request a quotation for WGF / WGF-D (N)TSFLCGEWOEU
Application engineer · Medium-voltage port & stockyard reeling cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/wg-wgf-d-mv-flat-epr-reeling-cable-ntsflcgewoeu/#template-selection
An application engineer replies within 2 business hours.

## Sizes
WGF / WGF-D Flat MV Reeling Cable (N)TSFLCGEWOEU (3.6/6–8.7/15 kV) – Flat geometry & mechanical loads (21 configs) (21)
TEBAOFLEX ¦ https://tebaoflex.com/cables/wg-wgf-d-mv-flat-epr-reeling-cable-ntsflcgewoeu/ ¦ Data revision 2026-10-20
Typical values for this cable type. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Height d × Width B | Max Height d | Max Width B | Cu number | Weight ≈ | Permitted pull | Min Bend D (1.5×d) | Series
| WGF 3.6/6 kV · 3 × 35 + 3 × 25/3E | 25.5–28.5 × 68.2–72.2 | 28.5 | 72.2 | 1346 | 3250 | 1575 | 43 | WGF Flat Power · 3.6/6 kV (5 sizes)
| WGF 3.6/6 kV · 3 × 50 + 3 × 25/3E | 28.0–31.0 × 74.1–78.1 | 31 | 78.1 | 1838 | 3980 | 2250 | 46 | WGF Flat Power · 3.6/6 kV (5 sizes)
| WGF 3.6/6 kV · 3 × 70 + 3 × 35/3E | 29.7–32.7 × 79.2–83.2 | 32.7 | 83.2 | 2573 | 4870 | 3150 | 49 | WGF Flat Power · 3.6/6 kV (5 sizes)
| WGF 3.6/6 kV · 3 × 95 + 3 × 50/3E | 31.7–34.7 × 84.7–89.7 | 34.7 | 89.7 | 3518 | 5920 | 4275 | 52 | WGF Flat Power · 3.6/6 kV (5 sizes)
| WGF 3.6/6 kV · 3 × 120 + 3 × 70/3E | 35.1–38.1 × 92.9–97.9 | 38.1 | 97.9 | 4515 | 7420 | 5400 | 57 | WGF Flat Power · 3.6/6 kV (5 sizes)
| WGF 8.7/15 kV · 3 × 35 + 3 × 25/3E | 28.7–31.7 × 76.2–80.2 | 31.7 | 80.2 | 1346 | 3820 | 1575 | 48 | WGF Flat Power · 8.7/15 kV (5 sizes)
| WGF 8.7/15 kV · 3 × 50 + 3 × 25/3E | 30.2–33.2 × 80.7–84.7 | 33.2 | 84.7 | 1807 | 4440 | 2250 | 50 | WGF Flat Power · 8.7/15 kV (5 sizes)
| WGF 8.7/15 kV · 3 × 70 + 3 × 35/3E | 33.3–36.3 × 87.5–92.5 | 36.3 | 92.5 | 2573 | 5610 | 3150 | 54 | WGF Flat Power · 8.7/15 kV (5 sizes)
| WGF 8.7/15 kV · 3 × 95 + 3 × 50/3E | 35.3–38.3 × 93.5–98.5 | 38.3 | 98.5 | 3518 | 6700 | 4275 | 57 | WGF Flat Power · 8.7/15 kV (5 sizes)
| WGF 8.7/15 kV · 3 × 120 + 3 × 70/3E | 37.3–40.3 × 99.5–104.5 | 40.3 | 104.5 | 4515 | 8000 | 5400 | 60 | WGF Flat Power · 8.7/15 kV (5 sizes)
| WGF-D 3.6/6 kV · 3 × 35 + 4 × 25/4E + 1 × (6 FO) | 24.5–27.5 × 83.5–88.5 | 27.5 | 88.5 | 1346 | 3700 | 1575 | 41 | WGF-D Flat Power + 6 FO · 3.6/6 kV (4 sizes)
| WGF-D 3.6/6 kV · 3 × 50 + 4 × 25/4E + 1 × (6 FO) | 27.0–30.0 × 90.9–95.9 | 30 | 95.9 | 1838 | 4530 | 2250 | 45 | WGF-D Flat Power + 6 FO · 3.6/6 kV (4 sizes)
| WGF-D 3.6/6 kV · 3 × 70 + 4 × 35/4E + 1 × (6 FO) | 28.7–31.7 × 97.7–102.7 | 31.7 | 102.7 | 2573 | 5590 | 3150 | 48 | WGF-D Flat Power + 6 FO · 3.6/6 kV (4 sizes)
| WGF-D 3.6/6 kV · 3 × 95 + 4 × 50/4E + 1 × (6 FO) | 30.6–33.6 × 105.3–110.3 | 33.6 | 110.3 | 3518 | 6720 | 4275 | 50 | WGF-D Flat Power + 6 FO · 3.6/6 kV (4 sizes)
| WGF-D 6/10 kV · 3 × 35 + 4 × 25/4E + 1 × (6 FO) | 25.3–28.3 × 86.7–91.7 | 28.3 | 91.7 | 1346 | 3870 | 1575 | 42 | WGF-D Flat Power + 6 FO · 6/10 kV (4 sizes)
| WGF-D 6/10 kV · 3 × 50 + 4 × 25/4E + 1 × (6 FO) | 27.8–30.8 × 94.1–99.1 | 30.8 | 99.1 | 1838 | 4730 | 2250 | 46 | WGF-D Flat Power + 6 FO · 6/10 kV (4 sizes)
| WGF-D 6/10 kV · 3 × 70 + 4 × 35/4E + 1 × (6 FO) | 29.5–32.5 × 100.9–105.9 | 32.5 | 105.9 | 2573 | 5800 | 3150 | 49 | WGF-D Flat Power + 6 FO · 6/10 kV (4 sizes)
| WGF-D 6/10 kV · 3 × 95 + 4 × 50/4E + 1 × (6 FO) | 31.4–34.4 × 108.5–113.5 | 34.4 | 113.5 | 3518 | 6940 | 4275 | 52 | WGF-D Flat Power + 6 FO · 6/10 kV (4 sizes)
| WGF-D 8.7/15 kV · 3 × 35 + 4 × 25/4E + 1 × (6 FO) | 28.5–31.5 × 96.6–101.9 | 31.5 | 101.9 | 1346 | 4610 | 1575 | 47 | WGF-D Flat Power + 6 FO · 8.7/15 kV (3 sizes)
| WGF-D 8.7/15 kV · 3 × 50 + 4 × 25/4E + 1 × (6 FO) | 30.0–33.0 × 102.9–107.9 | 33 | 107.9 | 1838 | 5340 | 2250 | 50 | WGF-D Flat Power + 6 FO · 8.7/15 kV (3 sizes)
| WGF-D 8.7/15 kV · 3 × 70 + 4 × 35/4E + 1 × (6 FO) | 31.7–33.7 × 109.7–114.7 | 33.7 | 114.7 | 2573 | 6460 | 3150 | 51 | WGF-D Flat Power + 6 FO · 8.7/15 kV (3 sizes)
Geometry d × B gives flat cable height d (min–max mm) and flat cable width B (min–max mm). Continuous flexing is permitted in ONE PLANE ONLY (bending over height d).
In the legacy WGF table (page 2), cable weights were printed with truncated trailing zeros after the German thousands dot (e.g. '3.25' for 3.250 = 3,250 kg/km and '6.7' for 6.700 = 6,700 kg/km); all weights are normalized to kg/km.
On the 70 mm² WGF rows, the legacy table prints '3 x 25 / 3E' while its 2,573 kg/km copper mass (identical to WGF-D 3 × 70 + 4 × 35/4E) and DIN VDE 0250-813 correspond to a 35 mm² total earth cross-section (3 × 35/3E).

## Electrical reference data
WGF / WGF-D Flat MV Reeling Cable (N)TSFLCGEWOEU (3.6/6–8.7/15 kV) – Electrical reference data (21)
TEBAOFLEX ¦ https://tebaoflex.com/cables/wg-wgf-d-mv-flat-epr-reeling-cable-ntsflcgewoeu/ ¦ Data revision 2026-10-20
Typical values for this cable type. Values for your order are confirmed in the quotation.
Designation | Rated U0/U | Max. DC R (20 °C) | Ref. Ampacity (30 °C) | AC Test Voltage | Series
WGF 3.6/6 kV · 3 × 35 + 3 × 25/3E | 3.6/6 kV | 0.565 | 162 | 11 kV AC (DIN VDE 0250-813) | WGF Flat Power · 3.6/6 kV (5 sizes)
WGF 3.6/6 kV · 3 × 50 + 3 × 25/3E | 3.6/6 kV | 0.393 | 202 | 11 kV AC (DIN VDE 0250-813) | WGF Flat Power · 3.6/6 kV (5 sizes)
WGF 3.6/6 kV · 3 × 70 + 3 × 35/3E | 3.6/6 kV | 0.277 | 250 | 11 kV AC (DIN VDE 0250-813) | WGF Flat Power · 3.6/6 kV (5 sizes)
WGF 3.6/6 kV · 3 × 95 + 3 × 50/3E | 3.6/6 kV | 0.210 | 301 | 11 kV AC (DIN VDE 0250-813) | WGF Flat Power · 3.6/6 kV (5 sizes)
WGF 3.6/6 kV · 3 × 120 + 3 × 70/3E | 3.6/6 kV | 0.164 | 352 | 11 kV AC (DIN VDE 0250-813) | WGF Flat Power · 3.6/6 kV (5 sizes)
WGF 8.7/15 kV · 3 × 35 + 3 × 25/3E | 8.7/15 kV | 0.565 | 162 | 24 kV AC (DIN VDE 0250-813) | WGF Flat Power · 8.7/15 kV (5 sizes)
WGF 8.7/15 kV · 3 × 50 + 3 × 25/3E | 8.7/15 kV | 0.393 | 202 | 24 kV AC (DIN VDE 0250-813) | WGF Flat Power · 8.7/15 kV (5 sizes)
WGF 8.7/15 kV · 3 × 70 + 3 × 35/3E | 8.7/15 kV | 0.277 | 250 | 24 kV AC (DIN VDE 0250-813) | WGF Flat Power · 8.7/15 kV (5 sizes)
WGF 8.7/15 kV · 3 × 95 + 3 × 50/3E | 8.7/15 kV | 0.210 | 301 | 24 kV AC (DIN VDE 0250-813) | WGF Flat Power · 8.7/15 kV (5 sizes)
WGF 8.7/15 kV · 3 × 120 + 3 × 70/3E | 8.7/15 kV | 0.164 | 352 | 24 kV AC (DIN VDE 0250-813) | WGF Flat Power · 8.7/15 kV (5 sizes)
WGF-D 3.6/6 kV · 3 × 35 + 4 × 25/4E + 1 × (6 FO) | 3.6/6 kV | 0.565 | 162 | 11 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 3.6/6 kV (4 sizes)
WGF-D 3.6/6 kV · 3 × 50 + 4 × 25/4E + 1 × (6 FO) | 3.6/6 kV | 0.393 | 202 | 11 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 3.6/6 kV (4 sizes)
WGF-D 3.6/6 kV · 3 × 70 + 4 × 35/4E + 1 × (6 FO) | 3.6/6 kV | 0.277 | 250 | 11 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 3.6/6 kV (4 sizes)
WGF-D 3.6/6 kV · 3 × 95 + 4 × 50/4E + 1 × (6 FO) | 3.6/6 kV | 0.210 | 301 | 11 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 3.6/6 kV (4 sizes)
WGF-D 6/10 kV · 3 × 35 + 4 × 25/4E + 1 × (6 FO) | 6/10 kV | 0.565 | 162 | 17 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 6/10 kV (4 sizes)
WGF-D 6/10 kV · 3 × 50 + 4 × 25/4E + 1 × (6 FO) | 6/10 kV | 0.393 | 202 | 17 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 6/10 kV (4 sizes)
WGF-D 6/10 kV · 3 × 70 + 4 × 35/4E + 1 × (6 FO) | 6/10 kV | 0.277 | 250 | 17 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 6/10 kV (4 sizes)
WGF-D 6/10 kV · 3 × 95 + 4 × 50/4E + 1 × (6 FO) | 6/10 kV | 0.210 | 301 | 17 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 6/10 kV (4 sizes)
WGF-D 8.7/15 kV · 3 × 35 + 4 × 25/4E + 1 × (6 FO) | 8.7/15 kV | 0.565 | 162 | 24 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 8.7/15 kV (3 sizes)
WGF-D 8.7/15 kV · 3 × 50 + 4 × 25/4E + 1 × (6 FO) | 8.7/15 kV | 0.393 | 202 | 24 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 8.7/15 kV (3 sizes)
WGF-D 8.7/15 kV · 3 × 70 + 4 × 35/4E + 1 × (6 FO) | 8.7/15 kV | 0.277 | 250 | 24 kV AC (DIN VDE 0250-813) | WGF-D Flat Power + 6 FO · 8.7/15 kV (3 sizes)
Maximum DC conductor resistance at 20 °C per IEC 60228 Table 3 for Class 5 tinned copper conductors.
Free-air reference ampacity at 30 °C ambient per DIN VDE 0298-4; apply monospiral reel layer derating factors.

## Technical data
WGF / WGF-D Flat MV Reeling Cable (N)TSFLCGEWOEU (3.6/6–8.7/15 kV) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/wg-wgf-d-mv-flat-epr-reeling-cable-ntsflcgewoeu/ ¦ Data revision 2026-10-20
Typical values for this cable type. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6–8.7/15 kV (3.6/6, 6/10 & 8.7/15 kV)
Key data | Reeling speed | 120 m/min (horiz. monospiral (1 plane))
Key data | Min. bend radius | D = 1.5 × d (1.5 × flat cable height d)
Key data | Flexing temp. | −35…+80 °C (fixed −50…+80 °C (90 °C cond.))
Key data | Tensile rating | 15 N/mm² (1,575–5,400 N across 35–120 mm²)
Key data | Configurations | 21 configs (10 WGF power + 11 WGF-D 6 FO)
Electrical | Rated voltage U0/U | 3.6/6.0 kV, 6.0/10.0 kV, and 8.7/15.0 kV
Electrical | Max. operating voltage AC | 4.2/7.2 kV (3.6/6 kV) · 6.9/12.0 kV (6/10 kV) · 10.2/18.0 kV (8.7/15 kV)
Electrical | Max. operating voltage DC | 5.4/10.8 kV (3.6/6 kV) · 9.0/18.0 kV (6/10 kV) · 13.0/26.0 kV (8.7/15 kV)
Electrical | AC test voltage (DIN VDE 0250-813) | 11 kV (3.6/6 kV) · 17 kV (6/10 kV) · 24 kV (8.7/15 kV) per DIN VDE 0250-813
Electrical | Current rating (DIN VDE 0298-4) | According to DIN VDE 0298-4 at 30 °C ambient (apply monospiral reel layer derating factors)
Thermal | Temperature, flexing | −35 °C to +80 °C (−25 °C to +80 °C in basic table; consult factory below −35 °C)
Thermal | Temperature, fixed installation | −50 °C to +80 °C
Thermal | Max. conductor temperature | +90 °C
Thermal | Short-circuit temperature | +250 °C
Mechanical | Max. travel speed | Up to 120 m/min horizontal (continuous bending in ONE PLANE ONLY)
Mechanical | Max. tensile load (dynamic) | 15 N/mm² of phase conductor cross-section (1,575–5,400 N across 35–120 mm²)
Mechanical | Min. bending diameter, flexing | Minimum bend diameter D = 1.5 × flat cable height (d) in one plane only; no multi-plane or S-shape bending
Optical | Optical fibre unit (WGF-D) | WGF-D: 1 × (6 FO) integrated optical fibre core (G9/125 SM, G50/125 MM, or G62.5/125 MM) laid parallel with the four-part earth system
Optical | Optical attenuation (850 / 1300 nm) | G9/125 SM: ≤ 0.4 dB/km (1300 nm) · G50/125 MM: ≤ 2.8 dB/km (850 nm), ≤ 0.8 dB/km (1300 nm) · G62.5/125 MM: ≤ 3.3 dB/km (850 nm), ≤ 0.9 dB/km (1300 nm)
Resistance | Chemical, sulfur & urea resistance | Resistant to oil, ozone, UV, humidity, moisture, sulfur, and urea; LBS-free and silicone-free (not halogen-free)
Resistance | Flame retardance | Low flammability / flame-retardant per IEC 60332-1-2
Standards | Cable standard & designation | (N)TSFLCGEWOEU / (N)TSFLCGEWOEU-FO according to DIN VDE 0250
Standards | Conductor standard | Flexible tinned electrolytic copper, Class 5 per DIN VDE 0295 / IEC 60228
Standards | Core & earth arrangement | Cores laid in parallel; protective earth concentrically split (3E on WGF; 4E + 1 × 6 FO additional core on WGF-D)

## Construction
WGF / WGF-D Flat MV Reeling Cable (N)TSFLCGEWOEU (3.6/6–8.7/15 kV) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/wg-wgf-d-mv-flat-epr-reeling-cable-ntsflcgewoeu/ ¦ Data revision 2026-10-20
Typical values for this cable type. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible Class 5 tinned copper conductor | Tinned electrolytic copper, flexible Class 5 per DIN VDE 0295 / IEC 60228
2 | Inner & outer semiconductive field control (CGE) | Inner semiconductive conductor screen and outer semiconductive insulation screen over each phase core
3 | Special HV-EPR core insulation | High-voltage ethylene-propylene rubber (EPR) compound according to VDE
4 | Concentric split protective earth (3E / 4E) | Tinned copper earth conductor equally split and applied concentrically over the phase cores (3 × S/3E in WGF; 4 × S/4E in WGF-D)
5 | Parallel 6-fibre optical unit (WGF-D only) | 1 × (6 FO) buffered optical fibre core laid in parallel within the flat profile (WGF-D series)
6 | Outer sheath (5GM5 Red) | Abrasion-resistant heavy-duty elastomer compound quality 5GM5 per DIN VDE 0207-21, red
| WGF (N)TSFLCGEWOEU · 3.6/6 & 8.7/15 kV (10 sizes) | 3 × 35 + 3 × 25/3E to 3 × 120 + 3 × 70/3E mm² flat MV power cable (25.5 × 68.2 mm to 40.3 × 104.5 mm)
| WGF-D (N)TSFLCGEWOEU-FO · 3.6/6, 6/10 & 8.7/15 kV (11 sizes) | 3 × 35 + 4 × 25/4E + 1 × (6 FO) to 3 × 95 + 4 × 50/4E + 1 × (6 FO) flat MV power + 6-fibre optical cable

## Quality and supply
WGF / WGF-D Flat MV Reeling Cable (N)TSFLCGEWOEU (3.6/6–8.7/15 kV) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/wg-wgf-d-mv-flat-epr-reeling-cable-ntsflcgewoeu/ ¦ Data revision 2026-10-20
Typical values for this cable type. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Medium-voltage AC dielectric test — 11 kV (3.6/6 kV), 17 kV (6/10 kV), 24 kV (8.7/15 kV) per DIN VDE 0250-813 | Every manufactured length
Type test | Vertical flame propagation — Low flammability / self-extinguishing per IEC 60332-1-2 | Type qualification
Type test | Chemical resistance (Sulfur & Urea) — Resistant to sulfur, urea, mineral oils, ozone, UV, and moisture (5GM5 compound) | Compound qualification
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX WGF / WGF-D (N)TSFLCGEWOEU [size] mm² [U0/U] kV
Supply | Delivery form: Custom monospiral reel lengths on heavy-duty timber drums; pre-assembled cable terminations available on request
Supply | Minimum order: 300 m to 500 m depending on cross-section and voltage class
Supply | Customs HS code: 8544.60