## Request a quote
Request a quotation for WK 137-Torsion FT4
Application engineer · wind turbine & torsion cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/wk-137-torsion-ft4-wind-turbine-nacelle-drip-loop-torsion-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
WK 137-Torsion FT4 Wind-Turbine Nacelle Drip-Loop Torsion Power Cable – Dimensions, weights & free-air ampacity (11)
TEBAOFLEX ¦ https://tebaoflex.com/cables/wk-137-torsion-ft4-wind-turbine-nacelle-drip-loop-torsion-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2277 (WTTC 1000 V) / UL 44 (RHW-2) / CSA FT4 / IEC 60332-3-22. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Metric / AWG | Rating | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | In air 30 °C A | Min. bend R mm | Series
| WK 137-Torsion FT4 1×35 mm² (2 AWG) | 1×35 mm² (2 AWG) | 1000 V | 14.2 | 336 | 465 | 198 | 85 | Single-Core 1000 V WTTC / RHW-2 Generator Drip-Loop Power Cables
| WK 137-Torsion FT4 1×50 mm² (1/0 AWG) | 1×50 mm² (1/0 AWG) | 1000 V | 16.5 | 480 | 635 | 245 | 99 | Single-Core 1000 V WTTC / RHW-2 Generator Drip-Loop Power Cables
| WK 137-Torsion FT4 1×70 mm² (2/0 AWG) | 1×70 mm² (2/0 AWG) | 1000 V | 18.6 | 672 | 855 | 305 | 112 | Single-Core 1000 V WTTC / RHW-2 Generator Drip-Loop Power Cables
| WK 137-Torsion FT4 1×95 mm² (3/0 AWG) | 1×95 mm² (3/0 AWG) | 1000 V | 21.2 | 912 | 1140 | 370 | 127 | Single-Core 1000 V WTTC / RHW-2 Generator Drip-Loop Power Cables
| WK 137-Torsion FT4 1×120 mm² (4/0 AWG) | 1×120 mm² (4/0 AWG) | 1000 V | 23.4 | 1152 | 1410 | 430 | 140 | Single-Core 1000 V WTTC / RHW-2 Generator Drip-Loop Power Cables
| WK 137-Torsion FT4 1×150 mm² (300 kcmil) | 1×150 mm² (300 kcmil) | 1000 V | 25.8 | 1440 | 1740 | 495 | 155 | Single-Core 1000 V WTTC / RHW-2 Generator Drip-Loop Power Cables
| WK 137-Torsion FT4 1×185 mm² (350 kcmil) | 1×185 mm² (350 kcmil) | 1000 V | 28.2 | 1776 | 2110 | 565 | 169 | Single-Core 1000 V WTTC / RHW-2 Generator Drip-Loop Power Cables
| WK 137-Torsion FT4 1×240 mm² (500 kcmil) | 1×240 mm² (500 kcmil) | 1000 V | 31.8 | 2304 | 2710 | 670 | 191 | Single-Core 1000 V WTTC / RHW-2 Generator Drip-Loop Power Cables
| WK 137-Torsion FT4 1×300 mm² (600 kcmil) | 1×300 mm² (600 kcmil) | 1000 V | 35 | 2880 | 3340 | 770 | 210 | Single-Core 1000 V WTTC / RHW-2 Generator Drip-Loop Power Cables
| WK 137-Torsion FT4 4G25 mm² (4×4 AWG) | 4G25 mm² (4×4 AWG) | 1000 V | 27.6 | 960 | 1420 | 138 | 166 | Multi-Core 1000 V WTTC / FT4 Nacelle Auxiliary Power Cables
| WK 137-Torsion FT4 4G50 mm² (4×1/0 AWG) | 4G50 mm² (4×1/0 AWG) | 1000 V | 35.8 | 1920 | 2680 | 205 | 215 | Multi-Core 1000 V WTTC / FT4 Nacelle Auxiliary Power Cables
Additional sizes from 16 mm² (6 AWG) up to 500 mm² (1000 kcmil) and 3- to 37-core control cables are also manufactured.

## Technical data
WK 137-Torsion FT4 Wind-Turbine Nacelle Drip-Loop Torsion Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/wk-137-torsion-ft4-wind-turbine-nacelle-drip-loop-torsion-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2277 (WTTC 1000 V) / UL 44 (RHW-2) / CSA FT4 / IEC 60332-3-22. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1000 V (WTTC) (600 V (UL RHW-2) · 0.6/1 kV IEC)
Key data | Yaw torsion | ±100° / metre (tested over > 5,000–10,000 cycles)
Key data | Temp. range | −40 to +90 °C (90 °C wet & dry (UL RHW-2/WTTC))
Key data | Flame rating | CSA FT4 / Cat A (UL 1685 FT4 vertical tray + IEC)
Key data | Conductor | Class 5 / K Cu (torsion-optimised bare/tinned Cu)
Key data | Min. bend R | 4 × OD (fixed) (6 × OD dynamic nacelle loop)
Electrical | Rated voltage | 1,000 V (UL 2277 WTTC / CSA) · 600 V (UL 44 RHW-2) · 0.6/1 kV (IEC 60502-1)
Electrical | Factory AC dielectric withstand test | 3.5 kV AC rms for 5 minutes
Thermal | Operating temperature range | −40 °C to +90 °C (torsion & fixed, wet or dry) · +250 °C short-circuit
Thermal | Thermal cycling & overload stability | Verified thermal ageing and short-circuit withstand per standard
Mechanical | Torsion angle & endurance qualification | ±100°/m (up to ±150°/m short-loop) over > 5,000 cycles down to −40 °C
Mechanical | Minimum bending radius | 4 × OD (static tower ladder) · 6 × OD (dynamic nacelle drip loop)
Resistance | Vertical tray flame retardance | CSA C22.2 No. 0.3 FT4, UL 1685 FT4 / IEEE 1202 & IEC 60332-3-22 Cat A
Resistance | Oil, UV & cold-impact resistance | UL Oil Res I & II (+60/+75 °C), 720 h Sunlight Resistant & −40 °C Cold
Standards | Dual North American & European approvals | cURus / cULus UL 2277 WTTC 1000V, UL 44 RHW-2, CSA FT4, CE & RoHS
Standards | Factory QA & material compliance | EN 10204 3.1 routine test certificate · RoHS 2 & REACH compliant
Identification | Dual metric & AWG/kcmil sizing | Marked with both metric (mm²) and North American (AWG / kcmil) sizes
Identification | Customs tariff (HS) | 8544.49

## Construction
WK 137-Torsion FT4 Wind-Turbine Nacelle Drip-Loop Torsion Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/wk-137-torsion-ft4-wind-turbine-nacelle-drip-loop-torsion-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2277 (WTTC 1000 V) / UL 44 (RHW-2) / CSA FT4 / IEC 60332-3-22. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Torsion-compensated fine-stranded copper (Class 5 / | IEC 60228 Class 5 / ASTM Class K annealed bare (or tinned) copper with long-pitch
2 | Low-friction torsion slip separator tape | Synthetic polyester/non-woven sliding tape over conductor
3 | Cross-linked EPR / HEPR dielectric (UL RHW-2) | 90 °C wet/dry thermoset Ethylene-Propylene Rubber compound
4 | Cross-linked CPE / Polychloroprene FT4 torsion jacket | Heavy-duty thermoset elastomer compound (Black, UV-stabilised, Oil Res I & II)
| WK 137-Torsion FT4 Single-Core (16–500 mm² / 6 AWG–1000 kcmil) | Main generator-to-transformer tower drop cables bundled in trefoil or spacer clamps
| WK 137-Torsion FT4 Multi-Core (3G–5G / Control) | Auxiliary nacelle power, yaw motor and pitch power feeders

## Quality and supply
WK 137-Torsion FT4 Wind-Turbine Nacelle Drip-Loop Torsion Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/wk-137-torsion-ft4-wind-turbine-nacelle-drip-loop-torsion-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 2277 (WTTC 1000 V) / UL 44 (RHW-2) / CSA FT4 / IEC 60332-3-22. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Type test | 20-year wind-turbine yaw torsion endurance test (±100°/m at −40 °C) — Zero strand breakage or jacket cracking after full life-cycle torsion simulation | Qualification type test
Routine test | 3.5 kV AC 5-min dielectric withstand & CSA FT4 vertical tray flame test — Zero breakdown; char height within CSA FT4 / IEEE 1202 limits | Every batch
Standard / approval | UL 2277 WTTC 1000 V & UL 44 RHW-2 Listed
Standard / approval | CSA C22.2 FT4 & IEC 60332-3-22 Cat A Flame Retardant
Standard / approval | −40 °C Cold Impact & ±100°/m Torsion Verified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX WK 137-TORSION FT4 <mm²/AWG> WTTC 1000V RHW-2 90C -40C OIL RES I/II FT4 CE
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP