## Request a quote
Request a quotation for Water-Cooled Two-Conductor Coaxial Cable
Application engineer · induction & metallurgical furnace cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/water-cooled-low-reactance-two-conductor-coaxial-high-frequency-induction-heating-feeder-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Water-Cooled Two-Conductor Coaxial Cable – Cross-section, frequency, current & cooling water flow (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/water-cooled-low-reactance-two-conductor-coaxial-high-frequency-induction-heating-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60519-3 / JB/T 6314 / VDE 0721. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Go + Return area | Voltage · Freq. | Hose OD ≈ mm | Rated current kA | Water flow L/min | Min. bend R mm | Series
| WC-2C-LR-2×95 | 2×95 mm² (Go & Return) | 1.5 kV · 1–10 kHz | 38 | 1.6 | 12 | 320 | High- & Medium-Frequency Coaxial Induction Leads (1–50 kHz · 2×95 to 2×240 mm²)
| WC-2C-LR-2×150 | 2×150 mm² (Go & Return) | 1.5 kV · 1–10 kHz | 45 | 2.5 | 16 | 380 | High- & Medium-Frequency Coaxial Induction Leads (1–50 kHz · 2×95 to 2×240 mm²)
| WC-2C-LR-2×240 | 2×240 mm² (Go & Return) | 2.0 kV · 0.5–10 kHz | 54 | 4 | 22 | 460 | High- & Medium-Frequency Coaxial Induction Leads (1–50 kHz · 2×95 to 2×240 mm²)
| WC-2C-LR-2×320 | 2×320 mm² (Go & Return) | 2.5 kV · 0.25–4 kHz | 62 | 5.5 | 28 | 530 | High-Current Melting Furnace Interleaved/Coaxial Leads (50 Hz–4 kHz · 2×320 to 2×630 mm²)
| WC-2C-LR-2×400 | 2×400 mm² (Go & Return) | 3.0 kV · 0.1–3 kHz | 68 | 7 | 34 | 580 | High-Current Melting Furnace Interleaved/Coaxial Leads (50 Hz–4 kHz · 2×320 to 2×630 mm²)
| WC-2C-LR-2×500 | 2×500 mm² (Go & Return) | 3.0 kV · 0.05–2 kHz | 75 | 9 | 42 | 650 | High-Current Melting Furnace Interleaved/Coaxial Leads (50 Hz–4 kHz · 2×320 to 2×630 mm²)
| WC-2C-LR-2×630 | 2×630 mm² (Go & Return) | 3.0 kV · 0.05–1 kHz | 84 | 11.5 | 52 | 720 | High-Current Melting Furnace Interleaved/Coaxial Leads (50 Hz–4 kHz · 2×320 to 2×630 mm²)
Manufactured to exact pin-to-pin length (1.5 m to 12 m) with customer-specified copper palm hole patterns and water fittings.

## Technical data
Water-Cooled Two-Conductor Coaxial Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/water-cooled-low-reactance-two-conductor-coaxial-high-frequency-induction-heating-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60519-3 / JB/T 6314 / VDE 0721. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Frequency | 50 Hz to 50 kHz (MF melting & HF tube/billet heat)
Key data | Architecture | 2-Cond. Coaxial (or 6-sector interleaved go/return)
Key data | Rated voltage | 800 to 3,000 V (tested to 6–10 kV AC rms)
Key data | Current rating | 1.5 to 11.5 kA (2×95 mm² up to 2×630 mm² TCu)
Key data | Magnetic force | Self-cancelling (zero external cable whip / kick)
Key data | Min. bend R | 8.5 × Hose OD (furnace hydraulic tilt & coil move)
Electrical | Operating frequency & voltage range | 50 Hz to 50 kHz · 800 V to 3,000 V AC rms (6–10 kV AC dielectric test)
Electrical | Loop inductance per unit length (L') | 0.04 to 0.08 µH/m (75–85 % lower than two separate single-core cables)
Electrical | Continuous MF/HF current rating | 1,500 A (2×95 mm²) to 11,500 A (2×630 mm²)
Thermal | Cooling water flow & temperature | 12 to 52 L/min deionised water (≤ 50 µS/cm) · Inlet ≤ 35 °C, Outlet ≤ 55 °C
Thermal | Thermal cycling & overload stability | Verified thermal ageing and short-circuit withstand per standard
Mechanical | Working & test hydrostatic pressure | 0.4–0.6 MPa working · 1.0–1.2 MPa routine hydrostatic proof test
Mechanical | Minimum dynamic bending radius | 8.5 × outer hose diameter during hydraulic furnace pour tilting
Resistance | Inter-conductor dielectric strength | 6.0 kV to 10.0 kV AC rms (50 Hz, 1 min) between Go and Return conductors
Resistance | Environmental & chemical durability | Resistant to moisture, industrial fluids and service ageing
Standards | Governing induction heating standards | IEC 60519-3 (Safety in induction heating), VDE 0721 & JB/T 6314
Standards | Factory QA & material compliance | EN 10204 3.1 routine test certificate · RoHS 2 & REACH compliant
Identification | Terminal head options | Parallel flat-palm, 90° elbow, coaxial flange or vacuum-feedthrough
Identification | Customs tariff (HS) | 8544.42 / 8514.90

## Construction
Water-Cooled Two-Conductor Coaxial Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/water-cooled-low-reactance-two-conductor-coaxial-high-frequency-induction-heating-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60519-3 / JB/T 6314 / VDE 0721. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Concentric / interleaved outer Return conductor (−I) | Concentric braided/stranded tinned copper rope (or 3+3 alternating ± sector ropes) bathed
2 | Inner cooling channel & central Go conductor (+I) | Perforated PTFE/EPDM coolant core surrounded by fine Ø 0.15–0.25 mm tinned copper
3 | High-dielectric inter-conductor barrier hose | Seamless extruded silicone rubber or peroxide-cured EPDM insulating tube + PTFE/polyimide
4 | Cord-reinforced slag-resistant EPDM outer cooling hose | Abrasion-, heat- and splash-resistant EPDM rubber hose (with optional fiberglass/silicone
| True Coaxial Water-Cooled (Inner Go + Concentric Outer Return) | Lowest possible inductance (0.04 µH/m) and zero external stray field for 1 kHz to 50 kHz converters
| 6-Sector Interleaved Symmetrical (+ − + − + −) | Symmetrical impedance between Go and Return phases for high-current 150 Hz to 3 kHz melting furnaces

## Quality and supply
Water-Cooled Two-Conductor Coaxial Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/water-cooled-low-reactance-two-conductor-coaxial-high-frequency-induction-heating-feeder-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60519-3 / JB/T 6314 / VDE 0721. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 6.0–10.0 kV AC inter-conductor dielectric & 1.0 MPa hydrostatic test — Zero breakdown between Go and Return; zero water leakage over 30 min | Every cable assembly
Sample test | 1 kHz / 10 kHz LCR bridge inductance (L') & AC resistance verify — Loop inductance L' ≤ 0.08 µH/m | Design & lot audit
Standard / approval | IEC 60519-3 Induction Heating Safety Compliant
Standard / approval | 100 % 6–10 kV Dielectric & 1.0 MPa Hydrostatic Tested
Standard / approval | CE & ISO 9001 Certified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | Stamped on Cu palms: TEBAOFLEX WC-2C-LR <size> L=<mm> Vmax=<V> SERIAL#
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP