## Request a quote
Request a quotation for YHKGXSFoyn
Application engineer · shaft & mining MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/yhkgxsfoyn-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YHKGXSFoyn Cable – Dimensions, weights & ampacity (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsfoyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section | Voltage | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | In air 25 °C A | Min. bend R mm | Series
| YHKGXSFoyn 3×25 3.6/6kV | 3×25 mm² | 3.6/6 kV | 36.5 | 675 | 2580 | 132 | 548 | 3.6/6 kV Round-Steel-Wire Armoured XLPE Shaft Mining Cables (YHKGXSFoyn)
| YHKGXSFoyn 3×35 3.6/6kV | 3×35 mm² | 3.6/6 kV | 39.2 | 945 | 3060 | 160 | 588 | 3.6/6 kV Round-Steel-Wire Armoured XLPE Shaft Mining Cables (YHKGXSFoyn)
| YHKGXSFoyn 3×50 3.6/6kV | 3×50 mm² | 3.6/6 kV | 42.6 | 1350 | 3760 | 194 | 639 | 3.6/6 kV Round-Steel-Wire Armoured XLPE Shaft Mining Cables (YHKGXSFoyn)
| YHKGXSFoyn 3×70 3.6/6kV | 3×70 mm² | 3.6/6 kV | 46.8 | 1890 | 4690 | 240 | 702 | 3.6/6 kV Round-Steel-Wire Armoured XLPE Shaft Mining Cables (YHKGXSFoyn)
| YHKGXSFoyn 3×95 3.6/6kV | 3×95 mm² | 3.6/6 kV | 51.2 | 2565 | 5780 | 288 | 768 | 3.6/6 kV Round-Steel-Wire Armoured XLPE Shaft Mining Cables (YHKGXSFoyn)
| YHKGXSFoyn 3×120 3.6/6kV | 3×120 mm² | 3.6/6 kV | 54.8 | 3240 | 6810 | 332 | 822 | 3.6/6 kV Round-Steel-Wire Armoured XLPE Shaft Mining Cables (YHKGXSFoyn)
| YHKGXSFoyn 3×150 3.6/6kV | 3×150 mm² | 3.6/6 kV | 59 | 4050 | 8190 | 378 | 885 | 3.6/6 kV Round-Steel-Wire Armoured XLPE Shaft Mining Cables (YHKGXSFoyn)
| YHKGXSFoyn 3×185 3.6/6kV | 3×185 mm² | 3.6/6 kV | 63 | 4995 | 9590 | 430 | 945 | 3.6/6 kV Round-Steel-Wire Armoured XLPE Shaft Mining Cables (YHKGXSFoyn)
| YHKGXSFoyn 3×240 3.6/6kV | 3×240 mm² | 3.6/6 kV | 68.5 | 6480 | 11780 | 505 | 1028 | 3.6/6 kV Round-Steel-Wire Armoured XLPE Shaft Mining Cables (YHKGXSFoyn)
Screen-armoured YHKGXSekFoyn (3.6/6 kV to 12/20 kV) is also supplied for methane-hazard vertical shafts.

## Technical data
YHKGXSFoyn Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsfoyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6 kV (Umax = 7.2 kV (also 6/10 kV))
Key data | Armour (Fo) | Round steel wire (Ø 2.5–4.0 mm galv. steel wires)
Key data | Shaft angle | Up to 90° vert. (vertical shafts & 45°–90° drifts)
Key data | Insulation (XS) | XLPE (+90 °C) (250 °C short-circuit (5 s))
Key data | Outer sheath | PVC-yn (Red) (oxygen index OI ≥ 29 %)
Key data | Min. bend R | 15 × OD (fixed shaft & roadway installation)
Electrical | Rated voltage (U₀/U) | 3.6/6 kV (Umax = 7.2 kV) · also 6/10 kV (YHKGXSekFoyn)
Electrical | 50 Hz AC test voltage (5 min) | 11 kV AC rms
Electrical | Max. conductor DC resistance @ 20 °C | 0.727 Ω/km (25 mm²) to 0.0754 Ω/km (240 mm²)
Thermal | Max. conductor operating temperature | +90 °C continuous · +250 °C short-circuit (max. 5 s)
Thermal | Ambient temperature range | −30 °C to +70 °C (fixed) · −5 °C to +50 °C (installation)
Mechanical | Armour construction (Fo) | Galvanized round steel wires (Ø 2.5–4.0 mm, tensile 350–500 N/mm²)
Mechanical | Permissible roadway / shaft inclination | 0° to 90° vertical (mandatory for > 45° inclines and vertical shafts)
Mechanical | Minimum bending radius | 15 × OD (fixed installation)
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-EN 60332-3-22 Cat A (OI ≥ 29 %)
Resistance | Saline shaft-water resistance | Heavy zinc-coated armour wires + water-blocking yn PVC jacket
Standards | Governing standards | PN-G-90006, PN-93/E-90401 & IEC 60502-2
Standards | Mining shaft approval | WUG vertical shaft & steep-incline power feeder compliant
Identification | Polish code breakdown | YHKG + XS (XLPE) + Fo (galv. round steel wire armour) + yn (FR-PVC)
Identification | Outer sheath colour | Red (MV mining identification)
Identification | Customs tariff (HS) | 8544.60

## Construction
YHKGXSFoyn Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsfoyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Compacted stranded bare copper (RMC) | IEC 60228 Class 2 circular compacted copper (25 to 240 mm²)
2 | Cross-linked polyethylene (XS / XLPE) | +90 °C dry-cured XLPE dielectric compound
3 | Pressure-extruded anti-slump PVC inner bedding (Y) | Flame-retardant PVC inner covering gripping the cabled cores
4 | Galvanized round steel wire armour (Fo) + binder tape | Closed ring of Ø 2.5–4.0 mm hot-dip galvanized round steel wires with counter-wound steel
5 | Flame-retardant mining PVC outer sheath (yn) | Self-extinguishing red PVC compound (Oxygen Index ≥ 29 %)
| YHKGXSFoyn (Unscreened + Fo Wire Armour) | XLPE cores + PVC bedding + galvanized round steel wire armour (Fo) + red yn sheath
| YHKGXSekFoyn (+ Copper Screen ek + Fo) | Adds individual copper phase screens (ek) for methane-hazard vertical mine shafts

## Quality and supply
YHKGXSFoyn Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsfoyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 11 kV AC 5-minute high-voltage dielectric test — Zero breakdown across XLPE core insulation | Every drum
Sample test | Round steel wire tensile strength & IEC 60332-3-22 Cat A flame test — Wire tensile 350–500 N/mm²; Cat A vertical flame pass | Periodic audit
Standard / approval | PN-G-90006 & WUG Vertical Mine Shaft Approved
Standard / approval | PN-EN 60332-3-22 Category A Flame Retardant
Standard / approval | CE, RoHS 2 & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YHKGXSFoyn 3.6/6kV <size> PN-G-90006 CE
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP