## Request a quote
Request a quotation for YHKGXSFtZnyn
Application engineer · mining & MV power cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/yhkgxsftznyn-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YHKGXSFtZnyn Cable – Dimensions, weights & ampacity (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsftznyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section | Voltage | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | In air 25 °C A | Min. bend R mm | Series
| YHKGXSFtZnyn 3×16 3.6/6kV | 3×16 mm² | 3.6/6 kV | 31.5 | 432 | 1680 | 102 | 472 | 3.6/6 kV Flat-Steel-Tape Armoured XLPE Mining Cables (YHKGXSFtZnyn)
| YHKGXSFtZnyn 3×25 3.6/6kV | 3×25 mm² | 3.6/6 kV | 34.2 | 675 | 2090 | 132 | 513 | 3.6/6 kV Flat-Steel-Tape Armoured XLPE Mining Cables (YHKGXSFtZnyn)
| YHKGXSFtZnyn 3×35 3.6/6kV | 3×35 mm² | 3.6/6 kV | 36.8 | 945 | 2520 | 160 | 552 | 3.6/6 kV Flat-Steel-Tape Armoured XLPE Mining Cables (YHKGXSFtZnyn)
| YHKGXSFtZnyn 3×50 3.6/6kV | 3×50 mm² | 3.6/6 kV | 40.2 | 1350 | 3140 | 194 | 603 | 3.6/6 kV Flat-Steel-Tape Armoured XLPE Mining Cables (YHKGXSFtZnyn)
| YHKGXSFtZnyn 3×70 3.6/6kV | 3×70 mm² | 3.6/6 kV | 44 | 1890 | 3920 | 240 | 660 | 3.6/6 kV Flat-Steel-Tape Armoured XLPE Mining Cables (YHKGXSFtZnyn)
| YHKGXSFtZnyn 3×95 3.6/6kV | 3×95 mm² | 3.6/6 kV | 48.2 | 2565 | 4890 | 288 | 723 | 3.6/6 kV Flat-Steel-Tape Armoured XLPE Mining Cables (YHKGXSFtZnyn)
| YHKGXSFtZnyn 3×120 3.6/6kV | 3×120 mm² | 3.6/6 kV | 51.6 | 3240 | 5790 | 332 | 774 | 3.6/6 kV Flat-Steel-Tape Armoured XLPE Mining Cables (YHKGXSFtZnyn)
| YHKGXSFtZnyn 3×150 3.6/6kV | 3×150 mm² | 3.6/6 kV | 55.4 | 4050 | 6860 | 378 | 831 | 3.6/6 kV Flat-Steel-Tape Armoured XLPE Mining Cables (YHKGXSFtZnyn)
| YHKGXSFtZnyn 3×185 3.6/6kV | 3×185 mm² | 3.6/6 kV | 59.2 | 4995 | 8110 | 430 | 888 | 3.6/6 kV Flat-Steel-Tape Armoured XLPE Mining Cables (YHKGXSFtZnyn)
| YHKGXSFtZnyn 3×240 3.6/6kV | 3×240 mm² | 3.6/6 kV | 64.5 | 6480 | 10040 | 505 | 968 | 3.6/6 kV Flat-Steel-Tape Armoured XLPE Mining Cables (YHKGXSFtZnyn)
For methane-hazard roadways requiring individual phase screens, specify YHKGXSekFtZnyn.

## Technical data
YHKGXSFtZnyn Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsftznyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6 kV (Umax = 7.2 kV (also 0.6/1 kV))
Key data | Armour (FtZn) | Galv. steel tape (2 × 0.8 mm or 1.0 mm flat tapes)
Key data | Insulation (XS) | XLPE (+90 °C) (250 °C short-circuit (5 s))
Key data | Outer sheath | PVC-yn (Red) (oxygen index OI ≥ 29 %)
Key data | Max. incline | Up to 45° (horizontal & inclined drifts)
Key data | Min. bend R | 15 × OD (fixed armoured installation)
Electrical | Rated voltage (U₀/U) | 3.6/6 kV (Umax = 7.2 kV) · also 0.6/1 kV
Electrical | 50 Hz AC test voltage (5 min) | 11 kV AC rms
Electrical | Max. conductor DC resistance @ 20 °C | 1.15 Ω/km (16 mm²) to 0.0754 Ω/km (240 mm²)
Thermal | Max. conductor operating temperature | +90 °C continuous · +250 °C short-circuit (max. 5 s)
Thermal | Ambient temperature range | −30 °C to +70 °C (fixed) · −5 °C to +50 °C (installation)
Mechanical | Armour construction (FtZn) | 2 × galvanized flat steel tapes (100 % overlapping radial coverage)
Mechanical | Max. roadway inclination | Up to 45° slope (for 45°–90° shafts use YHKGXSFoyn)
Mechanical | Minimum bending radius | 15 × OD (fixed installation)
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-EN 60332-3-22 Cat A (OI ≥ 29 %)
Resistance | Corrosion protection | Hot-dip zinc-coated steel tapes under water-impervious yn PVC jacket
Standards | Governing standards | PN-G-90006, PN-93/E-90401 & IEC 60502-2
Standards | Mining authority compliance | WUG underground mine roadway & incline approved
Identification | Polish code breakdown | YHKG + XS (XLPE) + FtZn (galv. flat steel tape) + yn (FR-PVC)
Identification | Outer sheath colour | Red (3.6/6 kV) or Black (0.6/1 kV)
Identification | Customs tariff (HS) | 8544.60

## Construction
YHKGXSFtZnyn Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsftznyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Compacted stranded bare copper (RMC) | IEC 60228 Class 1 (16–25 mm²) or Class 2 (35–240 mm²) annealed copper
2 | Cross-linked polyethylene (XS / XLPE) | +90 °C XLPE dielectric compound
3 | Extruded PVC inner bedding (Y) | Flame-retardant PVC inner covering over laid-up cores
4 | Galvanized flat steel tape armour (FtZn) | Two helically applied hot-dip galvanized flat steel tapes (0.5–1.0 mm thick) with
5 | Flame-retardant mining PVC outer sheath (yn) | Self-extinguishing red PVC compound (Oxygen Index ≥ 29 %) | IEC 60332-3-22 Cat A bunched flame retardant
| YHKGXSFtZnyn (Unscreened + FtZn) | XLPE cores + PVC bedding + galvanized flat steel tape armour + red yn sheath
| YHKGXSekFtZnyn (+ Copper Screen ek + FtZn) | Adds individual copper phase screens (ek) for methane-hazard galleries

## Quality and supply
YHKGXSFtZnyn Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsftznyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 11 kV AC 5-minute dielectric withstand test — No breakdown across 3.6/6 kV XLPE insulation | Every drum
Sample test | Armour zinc coating & IEC 60332-3-22 Cat A flame test — Galvanized steel tape coating per PN-EN 10244-2; Cat A flame pass | Periodic audit
Standard / approval | PN-G-90006 & WUG Underground Mining Approved
Standard / approval | PN-EN 60332-3-22 Category A Flame Retardant
Standard / approval | CE, RoHS 2 & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YHKGXSFtZnyn 3.6/6kV <size> PN-G-90006 CE
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP