## Request a quote
Request a quotation for YHKGXSekyn
Application engineer · mining & MV power cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/yhkgxsekyn-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YHKGXSekyn Cable – Dimensions, weights & ampacity (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsekyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Phase / Screen | Voltage | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | In air 25 °C A | Min. bend R mm | Series
| YHKGXSekyn 3×25/16 3.6/6kV | 3×25 / 16 mm² | 3.6/6 kV | 34.5 | 830 | 1680 | 135 | 518 | 3.6/6 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×35/16 3.6/6kV | 3×35 / 16 mm² | 3.6/6 kV | 37.2 | 1100 | 2040 | 165 | 558 | 3.6/6 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×50/16 3.6/6kV | 3×50 / 16 mm² | 3.6/6 kV | 40.4 | 1510 | 2560 | 198 | 606 | 3.6/6 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×70/16 3.6/6kV | 3×70 / 16 mm² | 3.6/6 kV | 44.2 | 2060 | 3260 | 245 | 663 | 3.6/6 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×95/16 3.6/6kV | 3×95 / 16 mm² | 3.6/6 kV | 48.5 | 2740 | 4120 | 295 | 728 | 3.6/6 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×120/16 3.6/6kV | 3×120 / 16 mm² | 3.6/6 kV | 51.8 | 3420 | 4920 | 340 | 777 | 3.6/6 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×50/16 6/10kV | 3×50 / 16 mm² | 6/10 kV | 44 | 1525 | 2890 | 198 | 660 | 6/10 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×70/16 6/10kV | 3×70 / 16 mm² | 6/10 kV | 47.8 | 2075 | 3620 | 245 | 717 | 6/10 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×95/16 6/10kV | 3×95 / 16 mm² | 6/10 kV | 52 | 2760 | 4510 | 295 | 780 | 6/10 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×120/16 6/10kV | 3×120 / 16 mm² | 6/10 kV | 55.4 | 3440 | 5340 | 340 | 831 | 6/10 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×150/25 6/10kV | 3×150 / 25 mm² | 6/10 kV | 59.2 | 4330 | 6380 | 385 | 888 | 6/10 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
| YHKGXSekyn 3×185/25 6/10kV | 3×185 / 25 mm² | 6/10 kV | 63 | 5280 | 7520 | 440 | 945 | 6/10 kV Copper-Screened XLPE Mining Cables (YHKGXSekyn)
8.7/15 kV and 12/20 kV YHKGXSekyn cables are also manufactured to order.

## Technical data
YHKGXSekyn Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsekyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6 & 6/10 kV (also 8.7/15 & 12/20 kV)
Key data | Phase screen | Copper (ek) (individual Cu tape/wire screen)
Key data | Insulation (XS) | Triple XLPE (inner/outer semicon + +90 °C XLPE)
Key data | Outer sheath | PVC-yn (Red) (oxygen index OI ≥ 29 %)
Key data | Cross-sections | 3×25–240 mm² (with 16 or 25 mm² Cu screen)
Key data | Min. bend R | 15 × OD (screened 3-core MV feeder)
Electrical | Rated voltage (U₀/U) | 3.6/6 kV (Umax 7.2 kV) & 6/10 kV (Umax 12 kV); also 8.7/15 & 12/20 kV
Electrical | Partial discharge (PD) level | ≤ 5 pC at 1.73 × U₀ ambient routine test
Electrical | 50 Hz AC test voltage (5 min) | 11 kV AC (3.6/6 kV) · 15 kV AC (6/10 kV)
Thermal | Max. conductor operating temperature | +90 °C continuous · +250 °C short-circuit (max. 5 s)
Thermal | Max. copper screen short-circuit temp. | +350 °C adiabatic earth-fault limit
Mechanical | Minimum bending radius | 15 × OD (fixed screened multi-core cable)
Mechanical | Max. roadway inclination | Up to 15° (unarmoured)
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-EN 60332-3-22 Cat A (OI ≥ 29 %)
Resistance | Chemical & mine-water resistance | Acid, alkali and hydraulic oil resistant yn PVC jacket
Standards | Governing standards | PN-G-90006, ZN-TF & IEC 60502-2
Standards | Methane hazard compliance | Approved for WUG methane hazard degrees 'a', 'b' and 'c' (protected
Identification | Polish code breakdown | YHKG + XS (XLPE) + ek (Cu phase screen) + yn (flame-retardant PVC)
Identification | Outer sheath colour | Red (MV underground mining identification)
Identification | Customs tariff (HS) | 8544.60

## Construction
YHKGXSekyn Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsekyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Compacted stranded bare copper (RMC) | IEC 60228 Class 2 circular compacted copper (25 to 240 mm²)
2 | Inner & outer extruded semiconductive screens | Cross-linked semiconductive compound co-extruded with the XLPE wall
3 | Cross-linked polyethylene (XS / XLPE) | 2.5 mm wall (3.6/6 kV) or 3.4 mm wall (6/10 kV) dry-cured XLPE (+90 °C)
4 | Individual phase copper screen (ek) | Helical copper tapes or concentric copper wires + equalizing tape (16 or 25 mm²
5 | Flame-retardant mining PVC outer sheath (yn) | Self-extinguishing PVC compound (Oxygen Index ≥ 29 %) in Red over inner filling | IEC 60332-3-22 Cat A bunched flame retardant
| YHKGXSekyn 3.6/6 kV | 2.5 mm XLPE insulation wall + individual copper phase screens (ek)
| YHKGXSekyn 6/10 kV (and 8.7/15, 12/20 kV) | 3.4 mm to 5.5 mm triple-extruded XLPE wall + individual copper screens

## Quality and supply
YHKGXSekyn Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsekyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Partial discharge (≤ 5 pC at 1.73 U₀) & 11/15 kV AC test — Zero breakdown and PD ≤ 5 pC across triple-extruded XLPE cores | Every drum
Sample test | IEC 60332-3-22 Cat A bunched vertical flame test — Pass Category A vertical ladder flame test | Periodic audit
Standard / approval | PN-G-90006 & WUG Methane-Gallery Approved
Standard / approval | IEC 60502-2 Partial Discharge ≤ 5 pC Verified
Standard / approval | PN-EN 60332-3-22 Cat A Flame Retardant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YHKGXSekyn <voltage> <size> PN-G-90006 CE
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP