## Request a quote
Request a quotation for YHKGXSyn
Application engineer · mining & MV power cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/yhkgxsyn-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YHKGXSyn Cable – Dimensions, weights & ampacity (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section | Voltage | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | In air 25 °C A | Min. bend R mm | Series
| YHKGXSyn 3×16 3.6/6kV | 3×16 mm² | 3.6/6 kV | 27.5 | 432 | 1020 | 105 | 330 | 3.6/6 kV Three-Core Unarmoured XLPE Mining Cables (YHKGXSyn)
| YHKGXSyn 3×25 3.6/6kV | 3×25 mm² | 3.6/6 kV | 30.2 | 675 | 1340 | 135 | 362 | 3.6/6 kV Three-Core Unarmoured XLPE Mining Cables (YHKGXSyn)
| YHKGXSyn 3×35 3.6/6kV | 3×35 mm² | 3.6/6 kV | 32.8 | 945 | 1690 | 165 | 394 | 3.6/6 kV Three-Core Unarmoured XLPE Mining Cables (YHKGXSyn)
| YHKGXSyn 3×50 3.6/6kV | 3×50 mm² | 3.6/6 kV | 36 | 1350 | 2190 | 198 | 432 | 3.6/6 kV Three-Core Unarmoured XLPE Mining Cables (YHKGXSyn)
| YHKGXSyn 3×70 3.6/6kV | 3×70 mm² | 3.6/6 kV | 39.8 | 1890 | 2860 | 245 | 478 | 3.6/6 kV Three-Core Unarmoured XLPE Mining Cables (YHKGXSyn)
| YHKGXSyn 3×95 3.6/6kV | 3×95 mm² | 3.6/6 kV | 44 | 2565 | 3680 | 295 | 528 | 3.6/6 kV Three-Core Unarmoured XLPE Mining Cables (YHKGXSyn)
| YHKGXSyn 3×120 3.6/6kV | 3×120 mm² | 3.6/6 kV | 47.2 | 3240 | 4460 | 340 | 566 | 3.6/6 kV Three-Core Unarmoured XLPE Mining Cables (YHKGXSyn)
| YHKGXSyn 3×150 3.6/6kV | 3×150 mm² | 3.6/6 kV | 50.8 | 4050 | 5390 | 385 | 610 | 3.6/6 kV Three-Core Unarmoured XLPE Mining Cables (YHKGXSyn)
| YHKGXSyn 3×185 3.6/6kV | 3×185 mm² | 3.6/6 kV | 54.6 | 4995 | 6480 | 440 | 655 | 3.6/6 kV Three-Core Unarmoured XLPE Mining Cables (YHKGXSyn)
| YHKGXSyn 3×240 3.6/6kV | 3×240 mm² | 3.6/6 kV | 59.8 | 6480 | 8180 | 515 | 718 | 3.6/6 kV Three-Core Unarmoured XLPE Mining Cables (YHKGXSyn)
Current ratings based on +90 °C XLPE conductor temperature and +25 °C mine gallery ambient air.

## Technical data
YHKGXSyn Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 3.6/6 kV (Umax = 7.2 kV (3-core MV))
Key data | Insulation (XS) | XLPE (+90 °C) (250 °C short-circuit (5 s))
Key data | Outer sheath | PVC-yn (Red) (oxygen index OI ≥ 29 %)
Key data | Construction | Unarmoured (unscreened 3-core MV feeder)
Key data | Cross-sections | 3×16–240 mm² (IEC 60228 Class 1 or 2 Cu)
Key data | Min. bend R | 12 × OD (fixed installation in galleries)
Electrical | Rated voltage (U₀/U) | 3.6/6 kV (Umax = 7.2 kV) · also 0.6/1 kV on request
Electrical | 50 Hz AC test voltage (5 min) | 11 kV AC rms (for 3.6/6 kV rating)
Electrical | Max. conductor DC resistance @ 20 °C | 1.15 Ω/km (16 mm²) to 0.0754 Ω/km (240 mm²) per IEC 60228
Thermal | Max. conductor operating temperature | +90 °C continuous · +250 °C short-circuit (max. 5 s)
Thermal | Ambient temperature range | −30 °C to +70 °C (fixed) · −5 °C to +50 °C (laying)
Mechanical | Minimum bending radius | 12 × OD (fixed multi-core installation)
Mechanical | Max. permissible roadway inclination | Up to 15° (unarmoured); use FtZn to 45° or Fo to 90°
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-EN 60332-3-22 Cat A (Oxygen Index ≥ 29 %)
Resistance | Mine water & oil resistance | Resistant to acidic/alkaline mine water and hydraulic emulsions
Standards | Governing standards | PN-G-90006, PN-93/E-90401, ZN-TF & IEC 60502-2
Standards | Mining authority approval | WUG (Wyższy Urząd Górniczy) underground mine safety compliant
Identification | Polish code breakdown | Y (PVC) + HKG (mining) + XS (XLPE) + yn (flame-retardant PVC)
Identification | Outer sheath colour | Red (3.6/6 kV MV mining) or Black (0.6/1 kV LV mining)
Identification | Customs tariff (HS) | 8544.60

## Construction
YHKGXSyn Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Compacted stranded bare copper (RMC) | IEC 60228 / PN-EN 60228 Class 1 (RE, 16–25 mm²) or Class 2 (RMC, 35–240 mm²) annealed
2 | Cross-linked polyethylene (XS / XLPE) | Extruded +90 °C XLPE dielectric compound (2.5 mm radial wall at 3.6/6 kV)
3 | Flame-retardant non-hygroscopic inner filling | Extruded halogen-controlled Elastomer/PVC filling compound
4 | Flame-retardant mining PVC outer sheath (yn) | Special self-extinguishing PVC compound (Oxygen Index ≥ 29 %) in Red (3.6/6 kV MV
| YHKGXSyn (Unscreened, Unarmoured) | 3-core XLPE (XS) + flame-retardant PVC (yn) for non-gassy protected galleries
| YHKGXSekyn (+ Copper Phase Screen ek) | Adds individual copper screen over each XLPE phase for methane-hazard mines
| YHKGXSFtZnyn (+ Flat Steel Tape Armour) | Adds double galvanized flat steel tape armour (FtZn) for roadway crush protection

## Quality and supply
YHKGXSyn Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgxsyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-93/E-90401 / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 11 kV AC 5-minute high-voltage dielectric test — No breakdown across 3.6/6 kV XLPE core insulation | Every drum
Sample test | IEC 60332-3-22 Cat A vertical bunched flame & Oxygen Index test — Char ≤ 2.5 m; yn PVC sheath Oxygen Index ≥ 29 % | Type & audit test
Standard / approval | PN-G-90006 & WUG Underground Mining Compliant
Standard / approval | PN-EN 60332-3-22 Category A Flame Retardant
Standard / approval | CE, RoHS 2 & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YHKGXSyn 3.6/6kV <size> PN-G-90006 CE
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP