## Request a quote
Request a quotation for YHKGYFtZnyn
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for YHKGYFtZnyn.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/yhkgyftznyn-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YHKGYFtZnyn Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyftznyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYFtZnyn 0.6/1 kV to 6/10 kV Screened Steel-Tape Armoured Mining Cable). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| YHKGYFtZnyn 4 × 25 mm² 0.6/1 kV | 4 × 25 mm² (0.6/1 kV) | 25.0 mm² | 31.2 | 1010 | 2080 | 374 | Standard YHKGYFtZnyn configurations
| YHKGYFtZnyn 4 × 70 mm² 0.6/1 kV | 4 × 70 mm² (0.6/1 kV) | 70.0 mm² | 44 | 2760 | 4380 | 528 | Standard YHKGYFtZnyn configurations
| YHKGYFtZnyn 3 × 35 mm² 3.6/6 kV | 3 × 35 mm² (3.6/6 kV) | 35.0 mm² | 38.6 | 1120 | 2740 | 463 | Standard YHKGYFtZnyn configurations
| YHKGYFtZnyn 3 × 70 mm² 3.6/6 kV | 3 × 70 mm² (3.6/6 kV) | 70.0 mm² | 46.2 | 2190 | 4290 | 554 | Standard YHKGYFtZnyn configurations
| YHKGYFtZnyn 3 × 120 mm² 3.6/6 kV | 3 × 120 mm² (3.6/6 kV) | 120.0 mm² | 55.4 | 3690 | 6480 | 665 | Standard YHKGYFtZnyn configurations
| YHKGYFtZnyn 3 × 150 mm² 6/10 kV | 3 × 150 mm² (6/10 kV) | 150.0 mm² | 63.2 | 4620 | 8190 | 758 | Standard YHKGYFtZnyn configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90006 / ZN-TF (YHKGYFtZnyn 0.6/1 kV to 6/10 kV Screened Steel-Tape Armoured Mining Cable).

## Electrical & ampacity
YHKGYFtZnyn Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyftznyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYFtZnyn 0.6/1 kV to 6/10 kV Screened Steel-Tape Armoured Mining Cable). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
4 × 25 mm² (0.6/1 kV) | 0.78 | 102 | 92 | 2.88 | 1.72 | 3500
4 × 70 mm² (0.6/1 kV) | 0.272 | 195 | 176 | 8.05 | 0.62 | 3500
3 × 35 mm² (3.6/6 kV) | 0.554 | 135 | 122 | 4.03 | 1.22 | 11000
3 × 70 mm² (3.6/6 kV) | 0.272 | 202 | 182 | 8.05 | 0.6 | 11000
3 × 120 mm² (3.6/6 kV) | 0.161 | 280 | 252 | 13.8 | 0.36 | 11000
3 × 150 mm² (6/10 kV) | 0.129 | 318 | 286 | 17.25 | 0.29 | 17000
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per PN-G-90006 / ZN-TF (YHKGYFtZnyn 0.6/1 kV to 6/10 kV Screened Steel-Tape Armoured Mining Cable).

## Technical data
YHKGYFtZnyn Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyftznyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYFtZnyn 0.6/1 kV to 6/10 kV Screened Steel-Tape Armoured Mining Cable). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | PN-G-90006 (Polish underground mining specification)
Key data | Designation | YHKGYFtZnyn (H (screened) + FtZn (galv. steel tape))
Key data | Voltage ratings | 1 kV / 6 kV (0.6/1 kV, 3.6/6 kV & 6/10 kV)
Key data | Conductor | Class 5 / 2 (PN-EN 60228 stranded copper ('G'))
Key data | Armouring | Double Galv. (FtZn radial crush & impact armour)
Key data | Outer sheath | yn Mining FR-PVC (Self-extinguishing high-LOI PVC)
Electrical | Rated voltage U0/U | 0.6/1 kV · 3.6/6 kV · 6/10 kV AC
Electrical | AC dielectric test voltage | 3.5 kV (1 kV) · 11 kV (6 kV) · 17 kV (10
Electrical | Max. conductor operating temp. | +70 °C continuous · +160 °C short-circuit
Electrical | Screening system | H-type semi-conductive/metallic screen per
Thermal | Operating temperature range | -25 °C to +70 °C (fixed installation)
Thermal | Minimum installation temp. | -5 °C
Mechanical | Min. bending radius | 12 × overall diameter (D) for screened FtZn
Mechanical | Armour type | Double hot-dip galvanized flat steel tape
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-G-04035 mining flame
Resistance | Corrosion & crush resistance | Zinc-galvanized steel tapes ('FtZn') + dual
Standards | Primary specification | PN-G-90006 · ZN-TF / WUG underground mining
Standards | Conductor standard | PN-EN 60228
Identification | Core identification | Numbered phase cores or HD 308 S2 colour code
Identification | Outer sheath colour | Red (3.6/6 kV & 6/10 kV MV) or Black (0.6/1

## Construction
YHKGYFtZnyn Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyftznyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYFtZnyn 0.6/1 kV to 6/10 kV Screened Steel-Tape Armoured Mining Cable). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Multi-wire stranded copper conductor (G) | Flexible Class 5 (or Class 2) annealed copper per PN-EN 60228 | PN-G-90006 / PN-EN 60228
2 | PVC insulation (Y) with H semi-con | Insulating PVC compound with semi-conductive/electrostatic screen (H) and copper | PN-G-90006
3 | Extruded PVC inner bedding (Y) | Pressure-extruded PVC inner sheath cushioning the steel tapes | PN-G-90006
4 | Galvanized steel tape armour (FtZn) | Two helically applied hot-dip galvanized flat steel tapes (FtZn) | PN-G-90006
5 | Flame-retardant mining PVC outer | Self-extinguishing, oil-resistant mining PVC compound (yn) | PN-G-90006 / PN-EN 60332-1-2
| YHKGYFtZnyn 0.6/1 kV (3×16 to 4×150 mm²) | Screened steel-tape armoured 0.6/1 kV horizontal roadway feeder for gassy underground galleries.
| YHKGYFtZnyn 3.6/6 kV & 6/10 kV (3×25 to 3×185 mm²) | Screened steel-tape armoured MV trunk feeder for horizontal underground 6 kV and 10 kV roadways.

## Quality and supply
YHKGYFtZnyn Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyftznyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYFtZnyn 0.6/1 kV to 6/10 kV Screened Steel-Tape Armoured Mining Cable). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV / 11 kV / 17 kV AC dielectric test — 5 minutes AC withstand per PN-G-90006 | 100 % of drums
Routine test | Conductor DC resistance & H-screen/FtZn check — PN-EN 60228 resistance & screen/armour continuity | 100 % of drums
Sample test | Galvanized steel tape zinc coat & yn LOI — Hot-dip zinc adherence & self-extinguishing PVC check | Per production batch
Type test | PN-EN 60332-1-2 & PN-G-04035 mining flame test — Pass Polish underground mining fire propagation test | WUG / type approval
Standard / approval | PN-G-90006
Standard / approval | PN-EN 60332-1-2
Standard / approval | CE / WUG Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YHKGYFtZnyn 0.6/1KV / 3.6/6KV
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP