## Request a quote
Request a quotation for YHKGYekyn
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for YHKGYekyn.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/yhkgyekyn-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YHKGYekyn Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyekyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYekyn 0.6/1 kV, 3.6/6 kV & 6/10 kV Dual-Screened Mining Cable). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| YHKGYekyn 3 × 25 / 16 mm² 0.6/1 kV | 3 × 25 + 16 ek (1 kV) | 25.0 mm² | 27.8 | 890 | 1520 | 278 | Standard YHKGYekyn configurations
| YHKGYekyn 3 × 50 / 25 mm² 0.6/1 kV | 3 × 50 + 25 ek (1 kV) | 50.0 mm² | 34.6 | 1710 | 2540 | 346 | Standard YHKGYekyn configurations
| YHKGYekyn 3 × 35 / 16 mm² 3.6/6 kV | 3 × 35 + 16 ek (6 kV) | 35.0 mm² | 37.4 | 1190 | 2380 | 374 | Standard YHKGYekyn configurations
| YHKGYekyn 3 × 70 / 25 mm² 3.6/6 kV | 3 × 70 + 25 ek (6 kV) | 70.0 mm² | 44.8 | 2310 | 3760 | 448 | Standard YHKGYekyn configurations
| YHKGYekyn 3 × 95 / 35 mm² 6/10 kV | 3 × 95 + 35 ek (10 kV) | 95.0 mm² | 52.6 | 3180 | 5120 | 526 | Standard YHKGYekyn configurations
| YHKGYekyn 3 × 150 / 50 mm² 6/10 kV | 3 × 150 + 50 ek (10 kV) | 150.0 mm² | 60.8 | 4950 | 7280 | 608 | Standard YHKGYekyn configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90006 / ZN-TF (YHKGYekyn 0.6/1 kV, 3.6/6 kV & 6/10 kV Dual-Screened Mining Cable).

## Electrical & ampacity
YHKGYekyn Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyekyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYekyn 0.6/1 kV, 3.6/6 kV & 6/10 kV Dual-Screened Mining Cable). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
3 × 25 + 16 ek (1 kV) | 0.78 | 105 | 95 | 2.88 | 1.72 | 3500
3 × 50 + 25 ek (1 kV) | 0.386 | 158 | 142 | 5.75 | 0.86 | 3500
3 × 35 + 16 ek (6 kV) | 0.554 | 135 | 122 | 4.03 | 1.22 | 11000
3 × 70 + 25 ek (6 kV) | 0.272 | 202 | 182 | 8.05 | 0.6 | 11000
3 × 95 + 35 ek (10 kV) | 0.206 | 244 | 220 | 10.93 | 0.45 | 17000
3 × 150 + 50 ek (10 kV) | 0.129 | 318 | 286 | 17.25 | 0.29 | 17000
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per PN-G-90006 / ZN-TF (YHKGYekyn 0.6/1 kV, 3.6/6 kV & 6/10 kV Dual-Screened Mining Cable).

## Technical data
YHKGYekyn Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyekyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYekyn 0.6/1 kV, 3.6/6 kV & 6/10 kV Dual-Screened Mining Cable). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | PN-G-90006 (Polish underground mining specification)
Key data | Designation | YHKGYekyn (H (field screen) + ek (Cu fault screen))
Key data | Voltage ratings | 1 kV / 6 kV (0.6/1 kV, 3.6/6 kV & 6/10 kV)
Key data | Conductor | Class 5 / 2 (PN-EN 60228 stranded copper ('G'))
Key data | Copper screen | Cu Wires + (High earth-fault current capacity)
Key data | Outer sheath | yn Mining FR-PVC (Self-extinguishing high-LOI PVC)
Electrical | Rated voltage U0/U | 0.6/1 kV · 3.6/6 kV · 6/10 kV AC
Electrical | AC dielectric test voltage | 3.5 kV (1 kV) · 11 kV (6 kV) · 17 kV (10
Electrical | Max. conductor operating temp. | +70 °C continuous · +160 °C short-circuit
Electrical | Copper screen ('ek') cross-section | 16 mm², 25 mm², 35 mm², or 50 mm² per
Thermal | Operating temperature range | -25 °C to +70 °C (fixed installation)
Thermal | Minimum installation temp. | -5 °C
Mechanical | Min. bending radius | 10 × D (0.6/1 kV) · 12 × D (3.6/6 kV & 6/10
Mechanical | Construction | Unarmoured dual-screened ('H' + 'ek') for
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-G-04035 mining flame
Resistance | Mine water & oil resistance | Resistant to acidic/saline mine water and
Standards | Primary specification | PN-G-90006 · ZN-TF / WUG underground mining
Standards | Conductor standard | PN-EN 60228
Identification | Core identification | Numbered phase cores or HD 308 S2 colour code
Identification | Outer sheath colour | Red (3.6/6 kV & 6/10 kV MV) or Black/Yellow

## Construction
YHKGYekyn Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyekyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYekyn 0.6/1 kV, 3.6/6 kV & 6/10 kV Dual-Screened Mining Cable). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Multi-wire stranded copper conductor (G) | Flexible Class 5 (or Class 2) annealed copper per PN-EN 60228 | PN-G-90006 / PN-EN 60228
2 | PVC insulation (Y) with H semi-con | Special insulating PVC compound with semi-conductive electrostatic screen layers (H) | PN-G-90006
3 | Inner PVC bedding | Extruded PVC inner filler sheath | PN-G-90006
4 | Concentric copper wire & tape screen | Helically applied annealed copper wires bound with a counter-helical copper equalizing | PN-G-90006
5 | Flame-retardant mining PVC outer | Self-extinguishing, oil-resistant mining PVC compound (yn) | PN-G-90006 / PN-EN 60332-1-2
| YHKGYekyn 0.6/1 kV (3×16+ek to 4×120+ek mm²) | Low-voltage dual-screened flexible mining power cable for gassy galleries and VFD drives.
| YHKGYekyn 3.6/6 kV & 6/10 kV (3×25+ek to 3×185+ek mm²) | Medium-voltage unarmoured copper-screened feeder for movable underground transformer stations.

## Quality and supply
YHKGYekyn Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyekyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYekyn 0.6/1 kV, 3.6/6 kV & 6/10 kV Dual-Screened Mining Cable). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV / 11 kV / 17 kV AC dielectric test — 5 minutes AC withstand core-to-screen per PN-G-90006 | 100 % of drums
Routine test | Phase & 'ek' copper screen DC resistance — PN-EN 60228 & copper fault screen conductance check | 100 % of drums
Sample test | Partial discharge & yn sheath LOI test — MV dielectric integrity & self-extinguishing PVC check | Per production batch
Type test | PN-EN 60332-1-2 & PN-G-04035 mining flame test — Pass Polish underground mining fire propagation test | WUG / type approval
Standard / approval | PN-G-90006
Standard / approval | PN-EN 60332-1-2
Standard / approval | CE / WUG Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YHKGYekyn 0.6/1KV / 3.6/6KV
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP