## Request a quote
Request a quotation for YHKGYyn
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for YHKGYyn.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/yhkgyyn-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YHKGYyn Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYyn 0.6/1 kV & 3.6/6 kV H-Screened Mining Cable). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| YHKGYyn 4 × 10 mm² 0.6/1 kV | 4 × 10 mm² (0.6/1 kV) | 10.0 mm² | 21.4 | 410 | 820 | 214 | Standard YHKGYyn configurations
| YHKGYyn 4 × 25 mm² 0.6/1 kV | 4 × 25 mm² (0.6/1 kV) | 25.0 mm² | 28.6 | 995 | 1580 | 286 | Standard YHKGYyn configurations
| YHKGYyn 4 × 50 mm² 0.6/1 kV | 4 × 50 mm² (0.6/1 kV) | 50.0 mm² | 36.8 | 1970 | 2790 | 368 | Standard YHKGYyn configurations
| YHKGYyn 3 × 25 mm² 3.6/6 kV | 3 × 25 mm² (3.6/6 kV) | 25.0 mm² | 33.2 | 810 | 1790 | 332 | Standard YHKGYyn configurations
| YHKGYyn 3 × 50 mm² 3.6/6 kV | 3 × 50 mm² (3.6/6 kV) | 50.0 mm² | 39.8 | 1560 | 2840 | 398 | Standard YHKGYyn configurations
| YHKGYyn 3 × 95 mm² 3.6/6 kV | 3 × 95 mm² (3.6/6 kV) | 95.0 mm² | 48.6 | 2910 | 4620 | 486 | Standard YHKGYyn configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90006 / ZN-TF (YHKGYyn 0.6/1 kV & 3.6/6 kV H-Screened Mining Cable).

## Electrical & ampacity
YHKGYyn Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYyn 0.6/1 kV & 3.6/6 kV H-Screened Mining Cable). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
4 × 10 mm² (0.6/1 kV) | 1.91 | 60 | 54 | 1.15 | 4.2 | 3500
4 × 25 mm² (0.6/1 kV) | 0.78 | 102 | 92 | 2.88 | 1.72 | 3500
4 × 50 mm² (0.6/1 kV) | 0.386 | 154 | 139 | 5.75 | 0.86 | 3500
3 × 25 mm² (3.6/6 kV) | 0.78 | 110 | 99 | 2.88 | 1.65 | 11000
3 × 50 mm² (3.6/6 kV) | 0.386 | 162 | 146 | 5.75 | 0.84 | 11000
3 × 95 mm² (3.6/6 kV) | 0.206 | 240 | 216 | 10.93 | 0.45 | 11000
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per PN-G-90006 / ZN-TF (YHKGYyn 0.6/1 kV & 3.6/6 kV H-Screened Mining Cable).

## Technical data
YHKGYyn Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYyn 0.6/1 kV & 3.6/6 kV H-Screened Mining Cable). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | PN-G-90006 (Polish underground mining specification)
Key data | Designation | YHKGYyn (H = electrostatic / semi-conductive)
Key data | Voltage ratings | 0.6/1 kV & (LV & MV underground mining power)
Key data | Conductor | Class 5 / 2 (PN-EN 60228 stranded copper ('G'))
Key data | Screen system | H Electrostatic (Eliminates surface static & field stress)
Key data | Outer sheath | yn Mining FR-PVC (Self-extinguishing high-LOI PVC)
Electrical | Rated voltage U0/U | 0.6/1 kV AC & 3.6/6 kV AC
Electrical | AC dielectric test voltage | 3.5 kV AC (0.6/1 kV) · 11 kV AC (3.6/6 kV)
Electrical | Max. conductor operating temp. | +70 °C continuous · +160 °C short-circuit
Electrical | Electrostatic screening | H-type semi-conductive/metallic screen per
Thermal | Operating temperature range | -25 °C to +70 °C (fixed installation)
Thermal | Minimum installation temp. | -5 °C
Mechanical | Min. bending radius | 10 × overall diameter (D)
Mechanical | Sheath construction | Unarmoured double-sheathed (Y inner + yn
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-G-04035 mining flame
Resistance | Mine water & oil resistance | Resistant to acidic/saline mine water and
Standards | Primary specification | PN-G-90006 · ZN-TF / WUG underground mining
Standards | Conductor standard | PN-EN 60228
Identification | Core identification | HD 308 S2 colour code or numbered phase cores
Identification | Outer sheath colour | Black (0.6/1 kV) or Red/Yellow (3.6/6 kV)

## Construction
YHKGYyn Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYyn 0.6/1 kV & 3.6/6 kV H-Screened Mining Cable). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Multi-wire stranded copper conductor (G) | Flexible Class 5 (or Class 2) annealed copper per PN-EN 60228 | PN-G-90006 / PN-EN 60228
2 | PVC core insulation (Y) | Insulating polyvinyl chloride (PVC) compound | PN-G-90006
3 | Electrostatic / semi-conductive screen | Semi-conductive electrostatic screen layer (H) with copper continuity tape/wires | PN-G-90006
4 | Extruded PVC inner sheath (Y) | Pressure-extruded PVC inner sheath | PN-G-90006
5 | Flame-retardant mining PVC outer | Self-extinguishing, oil-resistant mining PVC compound (yn) | PN-G-90006 / PN-EN 60332-1-2
| YHKGYyn 0.6/1 kV (3×10 to 4×120 mm²) | Electrostatic-screened 0.6/1 kV unarmoured underground gallery power cable.
| YHKGYyn 3.6/6 kV (3×16 to 3×150 mm²) | Medium-voltage 3.6/6 kV H-screened unarmoured substation and gallery jumper cable.

## Quality and supply
YHKGYyn Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/yhkgyyn-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YHKGYyn 0.6/1 kV & 3.6/6 kV H-Screened Mining Cable). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV / 11 kV AC dielectric voltage test — 5 minutes AC withstand per PN-G-90006 | 100 % of drums
Routine test | Conductor DC resistance & H-screen continuity — PN-EN 60228 & electrostatic screen check | 100 % of drums
Sample test | yn sheath oxygen index (LOI) & wall check — Self-extinguishing mining PVC verification | Per production batch
Type test | PN-EN 60332-1-2 & PN-G-04035 mining flame test — Pass Polish underground mining fire propagation test | WUG / type approval
Standard / approval | PN-G-90006
Standard / approval | PN-EN 60332-1-2
Standard / approval | CE / WUG Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YHKGYyn 0.6/1KV / 3.6/6KV
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP