## Request a quote
Request a quotation for YKGYFoyn / YKGYFoyn-żo
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for YKGYFoyn / YKGYFoyn-żo.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ykgyfoyn-ykgyfoyn-zo-steel-wire-armoured-pvc-mining-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YKGYFoyn / YKGYFoyn-żo Steel-Wire Armoured PVC Mining Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ykgyfoyn-ykgyfoyn-zo-steel-wire-armoured-pvc-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-E-90401 (YKGYFoyn / YKGYFoyn-żo 0.6/1 kV Steel-Wire Armoured Mining Cable). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| YKGYFoyn-żo 5 × 4.0 mm² 0.6/1 kV | 5G 4.0 mm² | 4.0 mm² | 20.6 | 192 | 890 | 206 | Standard YKGYFoyn / YKGYFoyn-żo configurations
| YKGYFoyn-żo 5 × 10 mm² 0.6/1 kV | 5G 10 mm² | 10.0 mm² | 26.2 | 480 | 1490 | 262 | Standard YKGYFoyn / YKGYFoyn-żo configurations
| YKGYFoyn 4 × 25 mm² 0.6/1 kV | 4 × 25 mm² | 25.0 mm² | 31.8 | 960 | 2280 | 318 | Standard YKGYFoyn / YKGYFoyn-żo configurations
| YKGYFoyn 4 × 50 mm² 0.6/1 kV | 4 × 50 mm² | 50.0 mm² | 40.4 | 1920 | 3790 | 404 | Standard YKGYFoyn / YKGYFoyn-żo configurations
| YKGYFoyn 4 × 95 mm² 0.6/1 kV | 4 × 95 mm² | 95.0 mm² | 51.6 | 3648 | 6380 | 516 | Standard YKGYFoyn / YKGYFoyn-żo configurations
| YKGYFoyn 4 × 150 mm² 0.6/1 kV | 4 × 150 mm² | 150.0 mm² | 61.4 | 5760 | 9350 | 614 | Standard YKGYFoyn / YKGYFoyn-żo configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90006 / PN-E-90401 (YKGYFoyn / YKGYFoyn-żo 0.6/1 kV Steel-Wire Armoured Mining Cable).

## Electrical & ampacity
YKGYFoyn / YKGYFoyn-żo Steel-Wire Armoured PVC Mining Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ykgyfoyn-ykgyfoyn-zo-steel-wire-armoured-pvc-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-E-90401 (YKGYFoyn / YKGYFoyn-żo 0.6/1 kV Steel-Wire Armoured Mining Cable). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
5G 4.0 mm² | 4.95 | 34 | 31 | 0.46 | 10.9 | 3500
5G 10 mm² | 1.91 | 60 | 54 | 1.15 | 4.2 | 3500
4 × 25 mm² | 0.78 | 102 | 92 | 2.88 | 1.72 | 3500
4 × 50 mm² | 0.386 | 154 | 139 | 5.75 | 0.86 | 3500
4 × 95 mm² | 0.206 | 232 | 209 | 10.93 | 0.46 | 3500
4 × 150 mm² | 0.129 | 310 | 279 | 17.25 | 0.29 | 3500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per PN-G-90006 / PN-E-90401 (YKGYFoyn / YKGYFoyn-żo 0.6/1 kV Steel-Wire Armoured Mining Cable).

## Technical data
YKGYFoyn / YKGYFoyn-żo Steel-Wire Armoured PVC Mining Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ykgyfoyn-ykgyfoyn-zo-steel-wire-armoured-pvc-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-E-90401 (YKGYFoyn / YKGYFoyn-żo 0.6/1 kV Steel-Wire Armoured Mining Cable). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | PN-G-90006 (Polish underground mining specification)
Key data | Designation | YKGYFoyn / -żo (Fo = round galvanized steel wire armour)
Key data | Rated voltage | 0.6/1 kV AC (3.5 kV AC / 5 min dielectric test)
Key data | Conductor | Class 5 / 2 (PN-EN 60228 stranded copper ('G'))
Key data | Armouring | Round Steel Wire (Fo high-tensile shaft & incline armour)
Key data | Outer sheath | yn Mining FR-PVC (Self-extinguishing high-LOI PVC)
Electrical | Rated voltage U0/U | 0.6/1 kV AC (600/1000 V)
Electrical | AC dielectric test voltage | 3,500 V AC for 5 minutes
Electrical | Max. conductor operating temp. | +70 °C continuous · +160 °C short-circuit
Electrical | Min. insulation resistance @ 20 °C | ≥ 20 MΩ·km
Thermal | Operating temperature range | -25 °C to +70 °C (fixed installation)
Thermal | Minimum installation temp. | -5 °C
Mechanical | Min. bending radius | 10 × overall diameter (D) for round-wire
Mechanical | Armour type | Galvanized round steel wires ('Fo', pancerz
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-G-04035 mining flame
Resistance | Tensile & impact resistance | High axial tensile load capacity for
Standards | Primary specification | PN-G-90006 · PN-E-90401 · WUG underground
Standards | Conductor & armour standards | PN-EN 60228 · PN-EN 10257-1
Identification | Core identification | HD 308 S2 colour code (-żo or -o) or black
Identification | Outer sheath colour | Black (or Yellow mining visibility sheath)

## Construction
YKGYFoyn / YKGYFoyn-żo Steel-Wire Armoured PVC Mining Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ykgyfoyn-ykgyfoyn-zo-steel-wire-armoured-pvc-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-E-90401 (YKGYFoyn / YKGYFoyn-żo 0.6/1 kV Steel-Wire Armoured Mining Cable). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Multi-wire stranded copper conductor (G) | Flexible Class 5 (or Class 2 stranded) annealed copper per PN-EN 60228 | PN-G-90006 / PN-EN 60228
2 | PVC core insulation (Y) | Insulating polyvinyl chloride (PVC) compound (with or without -żo core) | PN-G-90006
3 | Extruded PVC inner bedding (Y) | Extruded PVC inner sheath cushioning the round wire armour | PN-G-90006
4 | Galvanized round steel wire armour (Fo) | Helical layer of galvanized round steel wires (Fo) bound with counter-helical steel tape | PN-G-90006 / PN-EN 10257-1
5 | Flame-retardant mining PVC outer | Self-extinguishing, oil-resistant mining PVC compound (yn) | PN-G-90006 / PN-EN 60332-1-2
| YKGYFoyn-żo (With Green-Yellow Core, 3×2.5 to 5×95 mm²) | Steel-wire armoured 0.6/1 kV shaft and roadway power/control cable with dedicated -żo PE core.
| YKGYFoyn / YKGYFoyn-o (Without Green-Yellow Core, 3×16 to 4×150 mm²) | Steel-wire armoured 3-phase and multi-core control cable using the Fo wire armour or external earth.

## Quality and supply
YKGYFoyn / YKGYFoyn-żo Steel-Wire Armoured PVC Mining Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ykgyfoyn-ykgyfoyn-zo-steel-wire-armoured-pvc-mining-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-E-90401 (YKGYFoyn / YKGYFoyn-żo 0.6/1 kV Steel-Wire Armoured Mining Cable). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC dielectric & insulation resistance — 3,500 V AC for 5 min per PN-G-90006 | 100 % of drums
Routine test | Conductor DC resistance & Fo wire continuity — PN-EN 60228 & galvanized steel wire armour check | 100 % of drums
Sample test | Fo steel wire tensile strength & zinc coat — PN-EN 10257-1 round armour wire verification | Per production batch
Type test | PN-EN 60332-1-2 & PN-G-04035 mining flame test — Pass Polish underground mining fire propagation test | WUG / type approval
Standard / approval | PN-G-90006 / PN-E-90401
Standard / approval | PN-EN 60332-1-2
Standard / approval | CE / WUG Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YKGYFoyn / YKGYFoyn-zo 0.6/1KV
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP