## Request a quote
Request a quotation for YKGYyn-żo
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for YKGYyn-żo.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ykgyyn-zo-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YKGYyn-żo Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ykgyyn-zo-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-E-90401 (YKGYyn-żo 0.6/1 kV Double-Sheathed Mining Power Cable). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| YKGYyn-żo 5 × 2.5 mm² 0.6/1 kV | 5G 2.5 mm² | 2.5 mm² | 14.6 | 120 | 325 | 117 | Standard YKGYyn-żo configurations
| YKGYyn-żo 4 × 6.0 mm² 0.6/1 kV | 4G 6.0 mm² | 6.0 mm² | 17.2 | 230 | 490 | 138 | Standard YKGYyn-żo configurations
| YKGYyn-żo 4 × 16 mm² 0.6/1 kV | 4G 16 mm² | 16.0 mm² | 23.8 | 614 | 1040 | 190 | Standard YKGYyn-żo configurations
| YKGYyn-żo 4 × 35 mm² 0.6/1 kV | 4G 35 mm² | 35.0 mm² | 31.4 | 1344 | 1960 | 251 | Standard YKGYyn-żo configurations
| YKGYyn-żo 4 × 70 mm² 0.6/1 kV | 4G 70 mm² | 70.0 mm² | 41.2 | 2688 | 3580 | 330 | Standard YKGYyn-żo configurations
| YKGYyn-żo 4 × 120 mm² 0.6/1 kV | 4G 120 mm² | 120.0 mm² | 51.8 | 4608 | 5890 | 414 | Standard YKGYyn-żo configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90006 / PN-E-90401 (YKGYyn-żo 0.6/1 kV Double-Sheathed Mining Power Cable).

## Electrical & ampacity
YKGYyn-żo Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ykgyyn-zo-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-E-90401 (YKGYyn-żo 0.6/1 kV Double-Sheathed Mining Power Cable). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
5G 2.5 mm² | 7.98 | 25 | 23 | 0.29 | 17.5 | 3500
4G 6.0 mm² | 3.3 | 42 | 38 | 0.69 | 7.3 | 3500
4G 16 mm² | 1.21 | 77 | 70 | 1.84 | 2.7 | 3500
4G 35 mm² | 0.554 | 126 | 114 | 4.03 | 1.25 | 3500
4G 70 mm² | 0.272 | 195 | 176 | 8.05 | 0.62 | 3500
4G 120 mm² | 0.161 | 272 | 245 | 13.8 | 0.37 | 3500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per PN-G-90006 / PN-E-90401 (YKGYyn-żo 0.6/1 kV Double-Sheathed Mining Power Cable).

## Technical data
YKGYyn-żo Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ykgyyn-zo-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-E-90401 (YKGYyn-żo 0.6/1 kV Double-Sheathed Mining Power Cable). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | PN-G-90006 (Polish underground mining specification)
Key data | Designation | YKGYyn-żo (Y (PVC) · K · G (Cl.5) · Y (inner) ·)
Key data | Rated voltage | 0.6/1 kV AC (3.5 kV AC / 5 min dielectric test)
Key data | Conductor | Class 5 Flexibl (PN-EN 60228 flexible copper)
Key data | Double sheath | Y Inner + yn (Gas-tight circular gland profile)
Key data | Protective core | -żo (Green-Yell (Integral PE protective conductor)
Electrical | Rated voltage U0/U | 0.6/1 kV AC (600/1000 V)
Electrical | AC dielectric test voltage | 3,500 V AC for 5 minutes
Electrical | Max. conductor operating temp. | +70 °C continuous · +160 °C short-circuit
Electrical | Min. insulation resistance @ 20 °C | ≥ 20 MΩ·km
Thermal | Operating temperature range | -25 °C to +70 °C (fixed) · -5 °C to +70 °C
Thermal | Minimum installation temp. | -5 °C
Mechanical | Min. bending radius | 8 × overall diameter (D)
Mechanical | Sheath construction | Double extruded sheath: PVC inner ('Y') +
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-G-04035 mining flame
Resistance | Mine water & oil resistance | Resistant to acidic/saline mine water and
Standards | Primary specification | PN-G-90006 · PN-E-90401 · WUG underground
Standards | Conductor standard | PN-EN 60228 Class 5
Identification | Core identification | Green-Yellow (-żo) + HD 308 S2 colours (or
Identification | Outer sheath colour | Black (or Yellow mining visibility sheath)

## Construction
YKGYyn-żo Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ykgyyn-zo-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-E-90401 (YKGYyn-żo 0.6/1 kV Double-Sheathed Mining Power Cable). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible Class 5 copper conductor (G) | Multi-wire flexible annealed copper per PN-EN 60228 Class 5 | PN-G-90006 / PN-EN 60228
2 | PVC core insulation (Y) with -żo core | Insulating polyvinyl chloride (PVC) compound; one core Green-Yellow (-żo) | PN-G-90006 / HD 308 S2
3 | Extruded PVC inner sheath (Y) | Pressure-extruded PVC inner sheath filling core interstices | PN-G-90006
4 | Flame-retardant mining PVC outer | Self-extinguishing, oil- and abrasion-resistant mining PVC compound (yn) with high | PN-G-90006 / PN-EN 60332-1-2
| YKGYyn-żo Multi-Core Control (5×1.5 to 24×2.5 mm²) | Double-sheathed flexible control and signalling cables for underground mining automation.
| YKGYyn-żo Gallery Power (4×6.0 to 4×120 mm² / 5×6.0 to 5×70 mm²) | 0.6/1 kV flexible 4-core and 5-core underground gallery power feeders.

## Quality and supply
YKGYyn-żo Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ykgyyn-zo-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / PN-E-90401 (YKGYyn-żo 0.6/1 kV Double-Sheathed Mining Power Cable). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC dielectric & spark test — 3,500 V AC for 5 min per PN-G-90006 | 100 % of drums
Routine test | Class 5 conductor DC resistance @ 20 °C — PN-EN 60228 Class 5 resistance verification | 100 % of drums
Sample test | Inner 'Y' & outer 'yn' sheath thickness & LOI — Double-sheath dimensions & oxygen index ≥ 29 % | Per production batch
Type test | PN-EN 60332-1-2 & PN-G-04035 mining flame test — Pass Polish underground mining fire propagation test | WUG / type approval
Standard / approval | PN-G-90006 / PN-E-90401
Standard / approval | PN-EN 60332-1-2
Standard / approval | CE / WUG Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YKGYyn-zo 0.6/1KV PN-G-90006
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP