## Request a quote
Request a quotation for YUHKGXSFtZnyn
Application engineer · armoured mining power cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/yuhkgxsftznyn-6-10kv-water-blocked-steel-tape-armoured-mining-mv-power-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
YUHKGXSFtZnyn 6/10 kV Water-Blocked Steel-Tape Mining Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yuhkgxsftznyn-6-10kv-water-blocked-steel-tape-armoured-mining-mv-power-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on PN-G-90006 / WT-TK-38 / IEC 60332-3-24. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| YUHKGXSFtZnyn 3×50 + 16 mm² 6/10 kV | 3 × 50 mm² + 16 mm² Central Earth | Class 2 compacted Cu + FtZn | 46.8 | 3690 | 22.5 | 700 | YUHKGXSFtZnyn Construction Schedule (-30 to +90 °C)
| YUHKGXSFtZnyn 3×70 + 16 mm² 6/10 kV | 3 × 70 mm² + 16 mm² Central Earth | Class 2 compacted Cu + FtZn | 51 | 4640 | 31.5 | 765 | YUHKGXSFtZnyn Construction Schedule (-30 to +90 °C)
| YUHKGXSFtZnyn 3×120 + 25 mm² 6/10 kV | 3 × 120 mm² + 25 mm² Central Earth | Class 2 compacted Cu + FtZn | 59.8 | 6890 | 54 | 895 | YUHKGXSFtZnyn Construction Schedule (-30 to +90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per PN-G-90006 / WT-TK-38 / IEC 60332-3-24.

## Electrical, optical & thermal p
YUHKGXSFtZnyn 6/10 kV Water-Blocked Steel-Tape Mining Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yuhkgxsftznyn-6-10kv-water-blocked-steel-tape-armoured-mining-mv-power-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on PN-G-90006 / WT-TK-38 / IEC 60332-3-24. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 50 mm² + 16 mm² Central Earth | 0.387 | 6/10 kV (195 A) | -30 to +90 °C
3 × 70 mm² + 16 mm² Central Earth | 0.268 | 6/10 kV (242 A) | -30 to +90 °C
3 × 120 mm² + 25 mm² Central Earth | 0.153 | 6/10 kV (335 A) | -30 to +90 °C
Every production length undergoes routine conductor DC resistance, high-voltage Spark/AC dielectric or OTDR continuity and dimensional verification.

## Technical data
YUHKGXSFtZnyn 6/10 kV Water-Blocked Steel-Tape Mining Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/yuhkgxsftznyn-6-10kv-water-blocked-steel-tape-armoured-mining-mv-power-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on PN-G-90006 / WT-TK-38 / IEC 60332-3-24. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 6/10 kV (6/10 kV & 3.6/6 kV wet roadway (≤45°))
Key data | Operating temp. | -30 to +90 °C (Continuous mining & industrial duty)
Key data | Min. bend radius | 15 × OD (Fixed installation / dynamic routing)
Key data | Core / conductor | 3×35–240 + E Cu (Class 2 Cu + central bare earth core)
Key data | Outer protection | U + FtZn + yn (Swelling tape + steel tape + red FR-PVC)
Key data | Standard | PN-G-90006 (PN-G-90006 / WT-TK-38 / IEC 60332-3-24)
Electrical | Rated voltage / transmission duty | 6/10 kV (PN-G-90006 / WT-TK-38 / IEC 60332-3-24)
Electrical | Core / conductor construction | Central Bare Earth Core (16 mm²) — Class 2 compacted circular bare copper earth conductor at cable center
Electrical | Primary dielectric / buffering | Phase Cores (3×70 mm² XLPE + H) — Class 2 bare copper + XLPE (XS) + semicon + individual copper tape screen
Thermal | Continuous operating temperature | -30 to +90 °C (mining & industrial service)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per PN-G-90006 / WT-TK-38 / IEC 60332-3-24
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Mining Flame-Retardant Sheath (yn) — Red high-oxygen-index (LOI ≥ 29%) Cat. C flame-retardant PVC outer jacket
Mechanical | Minimum bending radius | 15 × OD
Mechanical | Crush, impact & abrasion duty | Heavy-duty mining rock-cut, impact and tensile protection per PN-G-90006 / WT-TK-38 / IEC 60332-3-24
Resistance | Flame retardancy & mine fire safety | Self-extinguishing / flame-retardant mining jacket per PN-G-90006 / WT-TK-38 / IEC 60332-3-24
Resistance | Mine water, oil & chemical resistance | Resistant to acidic mine water, hydraulic oils and abrasion per PN-G-90006 / WT-TK-38 / IEC 60332-3-24
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | PN-G-90006 / WT-TK-38 / IEC 60332-3-24
Standards | Flame & environmental test standards | IEC 60332 / MSHA / EN 60794 / IEC 60228
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | YUHKGXSFtZnyn
Identification | Sheath colour & metre marking | Continuous metre-marked red mining outer sheath
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
YUHKGXSFtZnyn 6/10 kV Water-Blocked Steel-Tape Mining Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/yuhkgxsftznyn-6-10kv-water-blocked-steel-tape-armoured-mining-mv-power-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on PN-G-90006 / WT-TK-38 / IEC 60332-3-24. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Central Bare Earth Core (16 mm²) | Class 2 compacted circular bare copper earth conductor at cable center
2 | Phase Cores (3×70 mm² XLPE + H) | Class 2 bare copper + XLPE (XS) + semicon + individual copper tape screen
3 | PVC Inner Sheath & Swelling Tape (U) | Core filling + black PVC inner sheath (Y) + longitudinal water-blocking tapes
4 | Double Steel Tape Armour (FtZn) | Two helically lapped galvanized flat steel tapes for radial crush protection
5 | Mining Flame-Retardant Sheath (yn) | Red high-oxygen-index (LOI ≥ 29%) Cat. C flame-retardant PVC outer jacket
| YUHKGXSFtZnyn — Standard Mining Execution | Built to PN-G-90006 / WT-TK-38 / IEC 60332-3-24 with central bare earth core (16 mm²) and mining flame-retardant sheath (yn)
| YUHKGXSFtZnyn — Custom Drum Length & Gland Kit | Available in custom shaft/roadway drum lengths or pre-terminated assemblies
| YUHKGXSFtZnyn — Routine & Flame Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & flame test report

## Quality and supply
YUHKGXSFtZnyn 6/10 kV Water-Blocked Steel-Tape Mining Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/yuhkgxsftznyn-6-10kv-water-blocked-steel-tape-armoured-mining-mv-power-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on PN-G-90006 / WT-TK-38 / IEC 60332-3-24. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (PN-G-90006 / WT-TK-38 / IEC 60332-3-24) — DC resistance at 20 °C / optical attenuation and outer diameter within PN-G-90006 / WT-TK-38 / IEC 60332-3-24 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (PN-G-90006 / WT-TK-38 / IEC 60332-3-24) — Zero dielectric breakdown and verified insulation resistance over full production length | Every manufactured drum length
Type test | Flame propagation, mechanical crush & thermal ageing qualification (PN-G-90006 / WT-TK-38 / IEC 60332-3-24) — Verified flame retardancy, mechanical integrity and thermal endurance across -30 to +90 °C | Type qualification & periodic lot audit
Standard / approval | PN-G-90006 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YUHKGXSFtZnyn PN-G-90006 6/10 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel mine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shaft/reeling lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP