## Request a quote
Request a quotation for YY / YSLY
Application engineer · industrial control cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/yy-unscreened-control-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YY / YSLY Unscreened Control Cable – Dimensions & weights (27)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yy-unscreened-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0285 / BS EN 50525-2-51. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| YSLY-OZ 2×0.75 | 2×0.75 | 18 | 5 | 5.4 | 14 | 42 | 22 | 0.75 mm² Control Configurations (2 to 18 cores)
| YSLY-JZ 3G0.75 | 3G0.75 | 18 | 5.2 | 5.7 | 22 | 51 | 23 | 0.75 mm² Control Configurations (2 to 18 cores)
| YSLY-JZ 4G0.75 | 4G0.75 | 18 | 5.7 | 6.2 | 29 | 62 | 25 | 0.75 mm² Control Configurations (2 to 18 cores)
| YSLY-JZ 5G0.75 | 5G0.75 | 18 | 6.2 | 6.7 | 36 | 75 | 27 | 0.75 mm² Control Configurations (2 to 18 cores)
| YSLY-JZ 7G0.75 | 7G0.75 | 18 | 6.7 | 7.3 | 50 | 98 | 29 | 0.75 mm² Control Configurations (2 to 18 cores)
| YSLY-JZ 12G0.75 | 12G0.75 | 18 | 8.8 | 9.6 | 86 | 158 | 38 | 0.75 mm² Control Configurations (2 to 18 cores)
| YSLY-JZ 18G0.75 | 18G0.75 | 18 | 10.4 | 11.3 | 130 | 228 | 45 | 0.75 mm² Control Configurations (2 to 18 cores)
| YSLY-JZ 3G1.0 | 3G1.0 | 17 | 5.5 | 6 | 29 | 61 | 24 | 1.0 mm² Control Configurations (3 to 12 cores)
| YSLY-JZ 4G1.0 | 4G1.0 | 17 | 6 | 6.5 | 38 | 75 | 26 | 1.0 mm² Control Configurations (3 to 12 cores)
| YSLY-JZ 5G1.0 | 5G1.0 | 17 | 6.5 | 7.1 | 48 | 91 | 28 | 1.0 mm² Control Configurations (3 to 12 cores)
| YSLY-JZ 7G1.0 | 7G1.0 | 17 | 7.4 | 8 | 67 | 121 | 32 | 1.0 mm² Control Configurations (3 to 12 cores)
| YSLY-JZ 12G1.0 | 12G1.0 | 17 | 9.4 | 10.2 | 115 | 195 | 41 | 1.0 mm² Control Configurations (3 to 12 cores)
| YSLY-JZ 3G1.5 | 3G1.5 | 16 | 6.2 | 6.7 | 43 | 82 | 27 | 1.5 mm² Control & Signalling Configurations (3 to 25 cores)
| YSLY-JZ 4G1.5 | 4G1.5 | 16 | 6.6 | 7.2 | 58 | 102 | 29 | 1.5 mm² Control & Signalling Configurations (3 to 25 cores)
| YSLY-JZ 5G1.5 | 5G1.5 | 16 | 7.5 | 8.1 | 72 | 126 | 32 | 1.5 mm² Control & Signalling Configurations (3 to 25 cores)
| YSLY-JZ 7G1.5 | 7G1.5 | 16 | 8.2 | 8.9 | 101 | 166 | 36 | 1.5 mm² Control & Signalling Configurations (3 to 25 cores)
| YSLY-JZ 12G1.5 | 12G1.5 | 16 | 10.8 | 11.7 | 173 | 272 | 47 | 1.5 mm² Control & Signalling Configurations (3 to 25 cores)
| YSLY-JZ 18G1.5 | 18G1.5 | 16 | 12.7 | 13.8 | 259 | 395 | 55 | 1.5 mm² Control & Signalling Configurations (3 to 25 cores)
| YSLY-JZ 25G1.5 | 25G1.5 | 16 | 15.1 | 16.4 | 360 | 538 | 66 | 1.5 mm² Control & Signalling Configurations (3 to 25 cores)
| YSLY-JZ 3G2.5 | 3G2.5 | 14 | 7.5 | 8.1 | 72 | 128 | 32 | 2.5–16 mm² Control & Motor Supply Configurations
| YSLY-JZ 4G2.5 | 4G2.5 | 14 | 8.2 | 8.9 | 96 | 162 | 36 | 2.5–16 mm² Control & Motor Supply Configurations
| YSLY-JZ 5G2.5 | 5G2.5 | 14 | 9.1 | 9.9 | 120 | 198 | 40 | 2.5–16 mm² Control & Motor Supply Configurations
| YSLY-JZ 7G2.5 | 7G2.5 | 14 | 10.1 | 11 | 168 | 265 | 44 | 2.5–16 mm² Control & Motor Supply Configurations
| YSLY-JZ 4G4 | 4G4 | 12 | 9.8 | 10.6 | 154 | 245 | 42 | 2.5–16 mm² Control & Motor Supply Configurations
| YSLY-JZ 4G6 | 4G6 | 10 | 11.2 | 12.2 | 230 | 352 | 49 | 2.5–16 mm² Control & Motor Supply Configurations
| YSLY-JZ 4G10 | 4G10 | 8 | 14.4 | 15.6 | 384 | 575 | 62 | 2.5–16 mm² Control & Motor Supply Configurations
| YSLY-JZ 4G16 | 4G16 | 6 | 17.3 | 18.8 | 614 | 885 | 75 | 2.5–16 mm² Control & Motor Supply Configurations
Dimensions and weights are typical values per DIN VDE 0285 / BS EN 50525-2-51. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
YY / YSLY Unscreened Control Cable – Electrical & current ratings (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/yy-unscreened-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0285 / BS EN 50525-2-51. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single pair/core 30 °C, A | Multi-core bundle 30 °C, A
0.75 | 18 | 26 | 12.0 | 10.0
1 | 17 | 19.5 | 15.0 | 13.0
1.5 | 16 | 13.3 | 23.0 | 18.0
2.5 | 14 | 7.98 | 30.0 | 25.0
4 | 12 | 4.95 | 41.0 | 34.0
6 | 10 | 3.3 | 53.0 | 44.0
10 | 8 | 1.91 | 74.0 | 61.0
16 | 6 | 1.21 | 99.0 | 82.0
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / DIN VDE 0891-1. Apply grouping derating factors for multi-core control and signal bundles.

## Technical data
YY / YSLY Unscreened Control Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/yy-unscreened-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0285 / BS EN 50525-2-51. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/500 V (U0/U · 4.0 kV AC test voltage)
Key data | Temp. flexing | −5…+70 °C (−40…+80 °C fixed installation)
Key data | Bending radius | 4–7.5 × OD (4 × OD fixed · 7.5 × OD flexing)
Key data | Core coding | JZ / OZ / JB (White numbered + GN/YE or colour)
Key data | Flame test | IEC 60332-1-2 (Self-extinguishing PVC · CPR Eca)
Key data | Size range | 0.5–35 mm² (2 to 61 cores · Class 5 Cu)
Electrical | Rated voltage U0/U | 300/500 V AC
Electrical | AC test voltage | 4000 V AC (50 Hz, 5 min)
Electrical | Insulation resistance | ≥ 20 MΩ·km at +20 °C
Electrical | Conductor stranding | IEC 60228 / DIN VDE 0295 Class 5 fine-stranded bare copper
Electrical | Current rating basis | DIN VDE 0298-4 (30 °C ambient in free air)
Thermal | Temperature, flexing | −5 °C to +70 °C (occasional movement)
Thermal | Temperature, fixed | −40 °C to +80 °C
Thermal | Max. conductor temperature | +70 °C (+80 °C fixed) continuous operation
Thermal | Short-circuit temperature | +160 °C max. (up to 5 s)
Mechanical | Min. bending radius, fixed | 4 × overall diameter
Mechanical | Min. bending radius, flexing | 7.5 × overall diameter (occasional free movement)
Mechanical | Max. tensile load | 15 N/mm² of total copper cross-section during installation
Mechanical | Mechanical duty | Light-to-medium mechanical stress in dry, damp or wet rooms
Resistance | Flame retardance | IEC 60332-1-2 / EN 60332-1-2 self-extinguishing · CPR Eca
Resistance | Oil & chemical resistance | Good resistance to industrial oils, greases and coolants
Resistance | Indoor & outdoor note | For indoor use; outdoor routing requires UV protection or black sheath
Standards | Construction basis | DIN VDE 0285-525-2-51 / BS EN 50525-2-51 / VDE 0245
Standards | Conductor standard | IEC 60228 / EN 60228 Class 5
Standards | Core identification | DIN VDE 0293-308 / EN 50334 (numbered) or HD 308 S2
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Silver-grey (RAL 7001); black or blue on request
Identification | Core identification | Black cores with white numbers + GN/YE (JZ) or without GN/YE (OZ)
Identification | Sheath marking | TEBAOFLEX YY / YSLY-JZ [Size] 300/500V IEC 60332-1-2 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
YY / YSLY Unscreened Control Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/yy-unscreened-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0285 / BS EN 50525-2-51. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor | Fine-stranded bare copper wire to IEC 60228 / DIN VDE 0295 Class 5 | IEC 60228 Class 5
2 | PVC core insulation | Special polyvinyl chloride compound Type TI2 (YI2 to DIN VDE 0207-4) | EN 50363-3 TI2
3 | Concentric core stranding | Cores stranded in concentric layers with short lay lengths (JZ with GN/YE, OZ without GN/YE) | DIN VDE 0293-308
4 | PVC outer sheath | Oil- and flame-resistant polyvinyl chloride compound Type TM2 (YM2), silver-grey RAL 7001 | EN 50363-4-1 TM2 · IEC 60332-1-2
| YSLY-JZ / YY-JZ (3G–61G) | Black cores with sequential white numbers + 1 green-yellow protective earth conductor
| YSLY-OZ / YY-OZ (2×–5×) | Black cores with sequential white numbers without green-yellow earth conductor
| YSLY-JB / YY-JB (3G–5G) | HD 308 S2 colour-coded power/control cores including green-yellow earth

## Quality and supply
YY / YSLY Unscreened Control Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/yy-unscreened-control-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0285 / BS EN 50525-2-51. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 4.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / DIN VDE 0285 / BS EN 50525-2-51 (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath material physical properties — DIN VDE 0285 / BS EN 50525-2-51 | Type approval
Standard / approval | DIN VDE 0285 / BS EN 50525-2-51
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YY / YSLY-JZ [Size] 300/500 V IEC 60332-1-2 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pair counts or sheath colours on request