## Request a quote
Request a quotation for YnOGY
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for YnOGY.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ynogy-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YnOGY Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ynogy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YnOGY 0.6/1 kV Flexible Mining Power & Control). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| YnOGY 4 × 2.5 mm² 0.6/1 kV | 4 × 2.5 mm² | 2.5 mm² | 12.4 | 96 | 225 | 74 | Standard YnOGY configurations
| YnOGY 7 × 2.5 mm² 0.6/1 kV | 7 × 2.5 mm² | 2.5 mm² | 15.2 | 168 | 345 | 91 | Standard YnOGY configurations
| YnOGY 4 × 6.0 mm² 0.6/1 kV | 4 × 6.0 mm² | 6.0 mm² | 16.4 | 230 | 440 | 98 | Standard YnOGY configurations
| YnOGY 4 × 16 mm² 0.6/1 kV | 4 × 16 mm² | 16.0 mm² | 22.8 | 614 | 960 | 137 | Standard YnOGY configurations
| YnOGY 4 × 35 mm² 0.6/1 kV | 4 × 35 mm² | 35.0 mm² | 30.2 | 1344 | 1840 | 181 | Standard YnOGY configurations
| YnOGY 1 × 70 mm² 0.6/1 kV (Locomotive) | 1 × 70 mm² | 70.0 mm² | 17.6 | 672 | 830 | 106 | Standard YnOGY configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90006 / ZN-TF (YnOGY 0.6/1 kV Flexible Mining Power & Control).

## Electrical & ampacity
YnOGY Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ynogy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YnOGY 0.6/1 kV Flexible Mining Power & Control). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
4 × 2.5 mm² | 7.98 | 25 | 23 | 0.29 | 17.5 | 3500
7 × 2.5 mm² | 7.98 | 20 | 18 | 0.29 | 17.5 | 3500
4 × 6.0 mm² | 3.3 | 42 | 38 | 0.69 | 7.3 | 3500
4 × 16 mm² | 1.21 | 77 | 70 | 1.84 | 2.7 | 3500
4 × 35 mm² | 0.554 | 126 | 114 | 4.03 | 1.25 | 3500
1 × 70 mm² | 0.272 | 235 | 212 | 8.05 | 0.58 | 3500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per PN-G-90006 / ZN-TF (YnOGY 0.6/1 kV Flexible Mining Power & Control).

## Technical data
YnOGY Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ynogy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YnOGY 0.6/1 kV Flexible Mining Power & Control). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | PN-G-90006 (Polish underground mining specification)
Key data | Designation | YnOGY (Yn (FR-PVC) · O (portable) · G (Cl.5)
Key data | Rated voltage | 0.6/1 kV AC (600/1000 V power & control)
Key data | Conductor | Class 5 Flexibl (PN-EN 60228 flexible stranded copper)
Key data | Outer sheath | Yn Mining FR-PVC (Self-extinguishing high-LOI PVC)
Key data | Operating temp. | -25 °C to +70 °C (+160 °C short-circuit rating)
Electrical | Rated voltage U0/U | 0.6/1 kV AC (600/1000 V)
Electrical | AC dielectric test voltage | 3,500 V AC (50 Hz) for 5 minutes
Electrical | Max. conductor operating temp. | +70 °C continuous · +160 °C short-circuit
Electrical | Min. insulation resistance @ 20 °C | ≥ 20 MΩ·km
Thermal | Operating temperature range | -25 °C to +70 °C (fixed) · -5 °C to +70 °C
Thermal | Minimum installation temp. | -5 °C
Mechanical | Min. bending radius | 6 × D (fixed) · 10 × D (flexible routing)
Mechanical | Conductor flexibility | Class 5 flexible multi-wire stranding ('G')
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-G-04035 mining flame
Resistance | Mine water & oil resistance | Resistant to acidic/saline mine water and
Standards | Primary specification | PN-G-90006 · ZN-TF / WUG (Higher Mining
Standards | Conductor standard | PN-EN 60228 Class 5
Identification | Core identification | HD 308 S2 colour code or black numbered cores
Identification | Outer sheath colour | Black (or Yellow / Blue mining

## Construction
YnOGY Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ynogy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YnOGY 0.6/1 kV Flexible Mining Power & Control). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible Class 5 copper conductor (G) | Multi-wire flexible annealed copper (bare or tinned) per PN-EN 60228 Class 5 | PN-G-90006 / PN-EN 60228
2 | PVC core insulation (Y) | Insulating polyvinyl chloride (PVC) compound Type TI1 / Y | PN-G-90006
3 | Core assembly binder tape | Polyester or non-woven separator tape over laid-up cores | PN-G-90006
4 | Flame-retardant mining PVC outer | Special self-extinguishing, oil-resistant mining PVC compound (Yn) with high oxygen index | PN-G-90006 / PN-EN 60332-1-2
| YnOGY Control & Signalling (4×1.5 to 24×2.5 mm²) | Multi-core flexible 0.6/1 kV control and telemetry cables for underground mining machinery.
| YnOGY Auxiliary Power & Locomotive (1×16 to 5×70 mm²) | Flexible Class 5 power interconnection cables for mine battery locomotives and mobile skids.

## Quality and supply
YnOGY Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ynogy-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YnOGY 0.6/1 kV Flexible Mining Power & Control). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC spark & dielectric voltage test — 3,500 V AC for 5 min per PN-G-90006 | 100 % of drums
Routine test | Class 5 conductor DC resistance @ 20 °C — PN-EN 60228 Class 5 maximum resistance limits | 100 % of drums
Sample test | Yn sheath oxygen index (LOI) & oil resistance — Self-extinguishing mining PVC verification | Per production batch
Type test | PN-EN 60332-1-2 & PN-G-04035 mining flame test — Pass Polish underground mining fire propagation test | WUG / type approval
Standard / approval | PN-G-90006
Standard / approval | PN-EN 60332-1-2
Standard / approval | CE / WUG Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YnOGY 0.6/1KV PN-G-90006 GORNICZY
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP