## Request a quote
Request a quotation for YnOGYek
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for YnOGYek.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ynogyek-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
YnOGYek Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ynogyek-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YnOGYek 0.6/1 kV Screened Flexible Mining Cable). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| YnOGYek 4 × 2.5 mm² 0.6/1 kV | 4 × 2.5 mm² + ek | 2.5 mm² | 15.2 | 148 | 340 | 122 | Standard YnOGYek configurations
| YnOGYek 7 × 2.5 mm² 0.6/1 kV | 7 × 2.5 mm² + ek | 2.5 mm² | 18 | 230 | 485 | 144 | Standard YnOGYek configurations
| YnOGYek 4 × 6.0 mm² 0.6/1 kV | 4 × 6.0 mm² + ek | 6.0 mm² | 19.4 | 310 | 610 | 155 | Standard YnOGYek configurations
| YnOGYek 4 × 16 mm² 0.6/1 kV | 4 × 16 mm² + ek | 16.0 mm² | 26.2 | 745 | 1220 | 210 | Standard YnOGYek configurations
| YnOGYek 4 × 35 mm² 0.6/1 kV | 4 × 35 mm² + ek | 35.0 mm² | 33.8 | 1540 | 2210 | 270 | Standard YnOGYek configurations
| YnOGYek 4 × 70 mm² 0.6/1 kV | 4 × 70 mm² + ek | 70.0 mm² | 43.6 | 2980 | 3920 | 349 | Standard YnOGYek configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per PN-G-90006 / ZN-TF (YnOGYek 0.6/1 kV Screened Flexible Mining Cable).

## Electrical & ampacity
YnOGYek Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ynogyek-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YnOGYek 0.6/1 kV Screened Flexible Mining Cable). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
4 × 2.5 mm² + ek | 7.98 | 25 | 23 | 0.29 | 17.5 | 3500
7 × 2.5 mm² + ek | 7.98 | 20 | 18 | 0.29 | 17.5 | 3500
4 × 6.0 mm² + ek | 3.3 | 42 | 38 | 0.69 | 7.3 | 3500
4 × 16 mm² + ek | 1.21 | 77 | 70 | 1.84 | 2.7 | 3500
4 × 35 mm² + ek | 0.554 | 126 | 114 | 4.03 | 1.25 | 3500
4 × 70 mm² + ek | 0.272 | 195 | 176 | 8.05 | 0.62 | 3500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per PN-G-90006 / ZN-TF (YnOGYek 0.6/1 kV Screened Flexible Mining Cable).

## Technical data
YnOGYek Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ynogyek-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YnOGYek 0.6/1 kV Screened Flexible Mining Cable). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | PN-G-90006 (Polish underground mining specification)
Key data | Designation | YnOGYek (ek = overall copper wire/tape screen)
Key data | Rated voltage | 0.6/1 kV AC (3.5 kV AC / 5 min dielectric test)
Key data | Conductor | Class 5 Flexibl (PN-EN 60228 flexible stranded copper)
Key data | Metallic screen | Cu Wires + (Fault-current & EMC earth screen)
Key data | Outer sheath | Yn Mining FR-PVC (Self-extinguishing high-LOI PVC)
Electrical | Rated voltage U0/U | 0.6/1 kV AC (600/1000 V)
Electrical | AC dielectric test voltage | 3,500 V AC for 5 minutes (core-to-core &
Electrical | Max. conductor operating temp. | +70 °C continuous · +160 °C short-circuit
Electrical | Screen fault conductivity | Copper wire + tape screen ('ek') sized per
Thermal | Operating temperature range | -25 °C to +70 °C (fixed) · -5 °C to +70 °C
Thermal | Minimum installation temp. | -5 °C
Mechanical | Min. bending radius | 8 × D (fixed) · 12 × D (flexible routing)
Mechanical | Conductor flexibility | Class 5 flexible multi-wire copper ('G')
Resistance | Flame retardance | PN-EN 60332-1-2 & PN-G-04035 mining flame
Resistance | Mine water & oil resistance | Resistant to saline mine water, oils, and
Standards | Primary specification | PN-G-90006 · ZN-TF / WUG underground mining
Standards | Conductor standard | PN-EN 60228 Class 5
Identification | Core identification | HD 308 S2 colour code or black numbered cores
Identification | Outer sheath colour | Black or Yellow mining PVC ('Yn')

## Construction
YnOGYek Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ynogyek-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YnOGYek 0.6/1 kV Screened Flexible Mining Cable). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible Class 5 copper conductor (G) | Multi-wire flexible annealed copper per PN-EN 60228 Class 5 | PN-G-90006 / PN-EN 60228
2 | PVC core insulation (Y) | Insulating polyvinyl chloride (PVC) compound | PN-G-90006
3 | Inner PVC bedding & semi-con layer | Extruded PVC inner filler sheath lapped with semi-conductive tape | PN-G-90006
4 | Concentric copper wire & tape screen | Helically applied annealed copper wires with counter-helical copper equalizing tape | PN-G-90006
5 | Flame-retardant mining PVC outer | Self-extinguishing, oil-resistant mining PVC compound (Yn) | PN-G-90006 / PN-EN 60332-1-2
| YnOGYek Screened Control & Pilot (4×2.5 to 19×2.5 mm²) | Screened flexible multi-core control and interlocking cables for underground flameproof switchgear.
| YnOGYek Screened Power (3×10+10 to 4×70 mm²) | 0.6/1 kV flexible power cables with concentric copper earth screen ('ek').

## Quality and supply
YnOGYek Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ynogyek-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on PN-G-90006 / ZN-TF (YnOGYek 0.6/1 kV Screened Flexible Mining Cable). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC dielectric test (core-to-screen) — 3,500 V AC for 5 min per PN-G-90006 | 100 % of drums
Routine test | Phase & 'ek' screen DC resistance @ 20 °C — PN-EN 60228 Class 5 & screen conductance check | 100 % of drums
Sample test | Yn sheath oxygen index (LOI) & tear check — Self-extinguishing mining PVC verification | Per production batch
Type test | PN-EN 60332-1-2 & PN-G-04035 mining flame test — Pass Polish underground mining fire propagation test | WUG / type approval
Standard / approval | PN-G-90006
Standard / approval | PN-EN 60332-1-2
Standard / approval | CE / WUG Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX YnOGYek 0.6/1KV PN-G-90006
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP